## Rezistenta termica
[7 empty] | Text | Viteza vint
BREVIAR DE CALCUL | [6 empty] | -18 | 6.4
Rezistenta termica specifica a elem. de constructie
ORIENTARI POSIBILE
Conform STAS 6472-1989 | [7 empty] | Rm | Ac | O1 | N | 5
PE1 | Perete exterior 1 | R = | 2.7337 | mp x K / W | D = | 5.6797 |  | 0.6 | 16 | O2 | S | -5
1 | Coeficient de convectie la interior | a i = | 8 | W / m x K | m = | 0.94102 |  | 0.7 | 14 | O3 | V | 0
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K |  |  |  | 0.8 | 12.5 | O4 | E | 0
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s |  | 0.9 | 11.5 | O5 | SV | -5
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K |  | 1 | 11 | O6 | SE | -5
1 | Tabla faltuita | 0.01 | 7850 | 58 | 0.00017241 | 125.6
2 | Placaj OSB | 0.02 | 600 | 0.17 | 0.11765 | 4.39
3 | Vata minerala bazaltica | 0.1 | 160 | 0.05 | 2 | 0.66
4 | Caramida GVP | 0.3 | 1700 | 0.75 | 0.4 | 8.95 |  | 1.4 | 8.8 | O8 | NE | 5
5 | Rigips | 0.015 | 1600 | 0.7 | 0.021429 | 8.24 |  | 1.6 | 8.2
6 | Glet | 0.005 | 500 | 0.18 | 0.027778 | 2.34
| TOTALURI: | 0.45 |  |  | 2.567
PE2 | Perete exterior 2 | R = | 2.7469 | mp x K / W | D = | 5.8003
1 | Coeficient de convectie la interior | a i = | 8 | W / m x K | m = | 0.93498
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K
1 | Sticla | 0.01 | 2500 | 0.75 | 0.013333 | 10.67
2 | Placaj OSB | 0.02 | 600 | 0.17 | 0.11765 | 4.39
3 | Vata minerala bazaltica | 0.1 | 160 | 0.05 | 2 | 0.66
4 | Caramida GVP | 0.3 | 1700 | 0.75 | 0.4 | 8.95
5 | Rigips | 0.015 | 1600 | 0.7 | 0.021429 | 8.24
6 | Glet | 0.005 | 500 | 0.18 | 0.027778 | 2.34
| TOTALURI: | 0.45 |  |  | 2.5802
PI | Perete interior | R = | 0.59187 | mp x K / W | D = | 3.5727
1 | Coeficient de convectie la interior | a i = | 8 | W / m x K | m = | 1.0464
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K
1 | Glet | 0.005 | 500 | 0.18 | 0.027778 | 2.34
2 | Tencuiala | 0.02 | 1600 | 0.7 | 0.028571 | 8.24
3 | Caramida | 0.25 | 1800 | 0.8 | 0.3125 | 9.51
4 | Tencuiala | 0.02 | 1600 | 0.7 | 0.028571 | 8.24
5 | Glet | 0.005 | 500 | 0.18 | 0.027778 | 2.34
| TOTALURI: | 0.3 |  |  | 0.4252
Psup. | Planseu superior | R = | 5.6393 | mp x K / W | D = | 4.752
1 | Coeficient de convectie la interior | a i = | 8 | W / m x K | m = | 0.9874
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K
1 | Gresogranit | 0.01 | 2800 | 3.48 | 0.0028736 | 25.45
2 | Sapa slab armata | 0.04 | 1800 | 0.93 | 0.043011 | 7.1
3 | Hidroizolatie | 0.02 | 600 | 0.17 | 0.11765 | 3.28
4 | Beton de panta | 0.03 | 1800 | 0.87 | 0.034483 | 9.75
5 | Folie PE | 0.002 | 300 | 0.09 | 0.022222 | 1.28
6 | Polistiren | 0.2 | 20 | 0.04 | 5 | 0.29
7 | Membrana bituminoasa | 0.02 | 600 | 0.17 | 0.11765 | 3.28
8 | Sapa | 0.03 | 1800 | 0.93 | 0.032258 | 7.1
9 | Placa beton armat | 0.15 | 2600 | 2.03 | 0.073892 | 17.9
10 | Rigips | 0.02 | 1600 | 0.7 | 0.028571 | 8.24
| TOTALURI: | 0.522 |  |  | 5.4726
Pint. | Planseu intermediar | R = | 1.3977 | mp x K / W | D = | 3.0751
1 | Coeficient de convectie la interior | a i = | 8 | W / m x K | m = | 1.0712
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K
1 | Rasina epoxidica | 0.02 | 1800 | 0.38 | 0.052632 | 8.49
2 | Dala flotanta | 0.05 | 1800 | 0.93 | 0.053763 | 7.1
3 | Folie PE | 0.002 | 300 | 0.09 | 0.022222 | 1.28
4 | Vata minerala bazaltica | 0.05 | 160 | 0.05 | 1 | 0.66
5 | Placa beton armat | 0.15 | 2600 | 2.03 | 0.073892 | 17.9
6 | Rigips | 0.02 | 1600 | 0.7 | 0.028571 | 8.24
| TOTALURI: | 0.292 |  |  | 1.2311
Pinf 1 | Planseu inferior 1 | R = | 4.3083 | mp x K / W | D = | 3.9919
1 | Coeficient de convectie la interior | a i = | 10 | W / m x K | m = | 1.0254
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K
1 | Rasina epoxidica | 0.02 | 1800 | 0.38 | 0.052632 | 8.49
2 | Sapa slab armata | 0.05 | 1800 | 0.93 | 0.053763 | 7.1
3 | Planseu beton armat | 0.1 | 2600 | 2.03 | 0.049261 | 17.9
4 | Folie PE | 0.002 | 300 | 0.09 | 0.022222 | 1.28
5 | Polistiren | 0.15 | 20 | 0.04 | 3.75 | 0.29
6 | Hidroizolatie | 0.02 | 600 | 0.17 | 0.11765 | 3.28
7 | Sapa slab armata | 0.04 | 1800 | 0.93 | 0.043011 | 7.1
8 | Folie PE | 0.002 | 300 | 0.09 | 0.022222 | 1.28
9 | Strat pietris | 0.015 | 1800 | 0.7 | 0.021429 | 8.74
10 | Pamant natural | 0.02 | 1600 | 0.58 | 0.034483 | 7.5
| TOTALURI: | 0.419 |  |  | 4.1667
Pinf 2 | Planseu inferior 2 | R = | 4.4378 | mp x K / W | D = | 4.032
1 | Coeficient de convectie la interior | a i = | 10 | W / m x K | m = | 1.0234
2 | Coeficient de convectie la exterior | a e = | 24 | W / m x K
STRATIFICATIE ELEMENT |  | Grosime | Densitate | Lambda | Rstrat | s
Nr | Material | m | kg/mc | W / m x K | mp x K / W | W / mp x K
1 | Gresogranit | 0.01 | 2800 | 3.48 | 0.0028736 | 25.45
2 | Hidroizolatie | 0.02 | 600 | 0.17 | 0.11765 | 3.28
3 | Beton de panta | 0.03 | 1100 | 0.26 | 0.11538 | 3.55
4 | Planseu beton armat | 0.1 | 2600 | 2.03 | 0.049261 | 17.9
5 | Folie PE | 0.002 | 300 | 0.09 | 0.022222 | 1.28
6 | Polistiren | 0.15 | 20 | 0.04 | 3.75 | 0.29
7 | Hidroizolatie | 0.02 | 600 | 0.17 | 0.11765 | 3.28
8 | Sapa slab armata | 0.04 | 1800 | 0.93 | 0.043011 | 7.1
9 | Folie PE | 0.002 | 300 | 0.09 | 0.022222 | 1.28
10 | Strat pietris | 0.015 | 1800 | 0.7 | 0.021429 | 8.74
11 | Pamant natural | 0.02 | 1600 | 0.58 | 0.034483 | 7.5
| TOTALURI: | 0.409 |  |  | 4.2962
| Aprilie 2014 |  |  |  | Întocmit,
| Cluj Napoca |  |  |  | ing.Bogdan Corabean

## necesar caldura
Denumire | Orientare | Latime | Inaltime | Suprafata | Numar | De scazut | In calcul | R' | m | Δt | Cm | mAΔt/R' | Ac | Ao | 1+(Ao+Ac)/100 | Qt*(1+(Ao+Ac)/100 | L | i | v | E | V | na | Q11 | Q12 | Qi | Q
|  | m | m | m2 |  | m2 | m2 | m2K/W |  | K |  | W |  |  |  | W | m |  | m/s |  | m3 | m/sm | W | W | W | W
PARTER
Laborator P1 P01 Ti=18 °C
PE1 | NE | 4.5 | 4 | 18 | 1 |  | 18 | 2.734 | 0.94 | 36 | 1 | 222.7944
PE1 | NV | 4.08 | 4 | 16.32 | 1 | 0.9375 | 15.3825 | 2.734 | 0.94 | 36 | 1 | 190.3964 |  |  |  |  | r= | 1.205
FE | NV | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 0.6 | 1.2 | 36 | 1 | 67.5 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 4.5 | 4.08 | 18.36 | 1 |  | 18.36 | 4.308 | 1.03 | 10 | 1 | 43.8969 |  |  |  |  | Rm= | 7.2304 |  |  |  | 1.5
[6 empty] | At= | 105.36 |  |  |  |  | 524.5878 | 5.4 | 5 | 1.104 | 579.1449 | 4 | 0.052 | 4 | 1 | 73.44 | 0.00022 | 1404.7591 | 31.5694 | 1404.7591 | 1983.904 | 27.0139
Incapere tampon P02 Ti=18 °C
PE1 | NE | 1.5 | 1.3 | 1.95 | 1 | 0.28 | 1.67 | 2.734 | 0.94 | 36 | 1 | 20.6704 |  |  |  |  | r= | 1.205
FE | NE | 0.8 | 0.35 | 0.28 | 1 |  | 0.28 | 0.6 | 1.2 | 36 | 1 | 20.16 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 1.5 | 4.08 | 6.12 | 1 |  | 6.12 | 4.308 | 1.03 | 10 | 1 | 14.6323 |  |  |  |  | Rm= | 36.92 |  |  |  | 1.5
[6 empty] | At= | 56.88 |  |  |  |  | 55.4627 | 5.4 | 5 | 1.104 | 61.2308 | 2.3 | 0.052 | 4 | 1 | 24.48 | 0.00022 | 468.253 | 18.1524 | 468.253 | 529.4838 | 21.6292
Echipamente P1 si P3 P03 Ti=15 °C
PE1 | SE | 2 | 2.7 | 5.4 | 1 |  | 5.4 | 2.734 | 0.94 | 33 | 1 | 61.2685
PE | NE | 2.5 | 2.7 | 6.75 | 1 | 1.89 | 4.86 | 2.734 | 0.94 | 33 | 1 | 55.1416
UE | NE | 0.9 | 2.1 | 1.89 | 1 |  | 1.89 | 0.6 | 1.2 | 33 | 1 | 124.74
PE1 | NV | 2 | 2.7 | 5.4 | 1 | 0.9375 | 4.4625 | 2.734 | 0.94 | 33 | 1 | 50.6316
FE | NV | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 0.6 | 1.2 | 33 | 1 | 61.875 |  |  |  |  | r= | 1.205
Pinf.2 | - | 2 | 2.5 | 5 | 1 |  | 5 | 4.438 | 1.02 | 5 | 1 | 5.7458 |  |  |  |  | Cp= | 1.005
Psup. | - | 2 | 2.5 | 5 | 1 |  | 5 | 5.639 | 0.99 | 33 | 1 | 28.9679 |  |  |  |  | Rm= | 2.9145 |  |  |  | 1.5
[6 empty] | At= | 34.3 |  |  |  |  | 388.3704 | 5.4 | 5 | 1.104 | 428.7609 | 10 | 0.052 | 4 | 1 | 13.5 | 0.00022 | 236.7088 | 72.3466 | 236.7088 | 665.4697 | 49.2941
Laborator P3 P04 Ti=18 °C
PE1 | NE | 4.35 | 4 | 17.4 | 1 | 0.9375 | 16.4625 | 2.734 | 0.94 | 36 | 1 | 203.7641 |  |  |  |  | r= | 1.205
FE | NE | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 0.6 | 1.2 | 36 | 1 | 67.5 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 5.425 | 4.08 | 22.134 | 1 |  | 22.134 | 4.308 | 1.03 | 10 | 1 | 52.9202 |  |  |  |  | Rm= | 13.36 |  |  |  | 1.5
[6 empty] | At= | 120.308 |  |  |  |  | 324.1843 | 5.4 | 5 | 1.104 | 357.8994 | 4 | 0.052 | 4 | 1 | 88.536 | 0.00022 | 1693.5151 | 31.5694 | 1693.5151 | 2051.4146 | 23.1704
Grup sanitar barbati P05 Ti=22 °C
PE1 | NE | 2.65 | 3 | 7.95 | 1 | 0.5625 | 7.3875 | 2.734 | 0.94 | 40 | 1 | 101.5984 |  |  |  |  | r= | 1.205
FE | NE | 0.75 | 0.75 | 0.5625 | 1 |  | 0.5625 | 0.6 | 1.2 | 40 | 1 | 45 |  |  |  |  | Cp= | 1.005
Pinf.2 | - | 2.65 | 3.95 | 10.4675 | 1 |  | 10.4675 | 4.438 | 1.02 | 14 | 1 | 33.6809 |  |  |  |  | Rm= | 13.4314 |  |  |  | 1.5
[6 empty] | At= | 60.535 |  |  |  |  | 180.2793 | 5.4 | 5 | 1.104 | 199.0284 | 3 | 0.052 | 4 | 1 | 31.4025 | 0.00022 | 667.4072 | 26.3078 | 667.4072 | 866.4356 | 27.5913
Grup sanitar femei P06 Ti=22 °C
PE1 | NE | 2.75 | 3 | 8.25 | 1 | 1.5 | 6.75 | 2.734 | 0.94 | 40 | 1 | 92.831
FE | NE | 2 | 0.75 | 1.5 | 1 |  | 1.5 | 0.6 | 1.2 | 40 | 1 | 120 |  |  |  |  | r= | 1.205
PI | - | 3.95 | 3 | 11.85 | 1 |  | 11.85 | 0.592 | 1.05 | 7 | 1 | 147.1242 |  |  |  |  | Cp= | 1.005
Pinf.2 | - | 2.65 | 3.95 | 10.4675 | 1 |  | 10.4675 | 4.438 | 1.02 | 14 | 1 | 33.6809 |  |  |  |  | Rm= | 6.1514 |  |  |  | 1.5
[6 empty] | At= | 60.535 |  |  |  |  | 393.6361 | 5.4 | 5 | 1.104 | 434.5742 | 5.5 | 0.052 | 4 | 1 | 31.4025 | 0.00022 | 667.4072 | 48.231 | 667.4072 | 1101.9815 | 35.0922
Centrala termica P07 Ti=15 °C
PE1 | NE | 3.75 | 4.75 | 17.8125 | 1 | 5.175 | 12.6375 | 2.734 | 0.94 | 33 | 1 | 143.3852
UE | NE | 1.5 | 3.45 | 5.175 | 1 |  | 5.175 | 0.6 | 1.2 | 33 | 1 | 341.55 |  |  |  |  | r= | 1.205
PI | - | 3.95 | 4.75 | 18.7625 | 1 |  | 18.7625 | 0.592 | 1.05 | 7 | 1 | 232.9466 |  |  |  |  | Cp= | 1.005
Pinf.2 | - | 3.75 | 3.95 | 14.8125 | 1 |  | 14.8125 | 4.438 | 1.02 | 7 | 1 | 23.8308 |  |  |  |  | Rm= | 4.5726 |  |  |  | 1
[6 empty] | At= | 102.775 |  |  |  |  | 741.7127 | 5.4 | 5 | 1.104 | 818.8508 | 9.9 | 0.052 | 4 | 1 | 70.3594 | 0.00022 | 822.4535 | 71.6231 | 822.4535 | 1641.3042 | 23.3274
Laborator P5 P09 Ti=18 °C
PE1 | NE | 6.125 | 4 | 24.5 | 1 | 1.7625 | 22.7375 | 2.734 | 0.94 | 36 | 1 | 281.4327
FE | NE | 0.75 | 2.35 | 1.7625 | 1 |  | 1.7625 | 0.6 | 1.2 | 36 | 1 | 126.9
PE1 | SE | 3.95 | 4 | 15.8 | 1 | 5.2875 | 10.5125 | 2.734 | 0.94 | 36 | 1 | 130.1181 |  |  |  |  | r= | 1.205
FE | SE | 0.75 | 2.35 | 1.7625 | 3 |  | 5.2875 | 0.6 | 1.2 | 36 | 1 | 380.7 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 6.13 | 3.95 | 24.2135 | 1 |  | 24.2135 | 4.308 | 1.03 | 10 | 1 | 57.8921 |  |  |  |  | Rm= | 4.7541 |  |  |  | 1
[6 empty] | At= | 129.027 |  |  |  |  | 977.0429 | 5.4 | 5 | 1.104 | 1078.6554 | 24.8 | 0.052 | 4 | 1 | 96.854 | 0.00022 | 1235.0811 | 195.7303 | 1235.0811 | 2313.7365 | 23.8889
Coridor P10 Ti=18 °C
PE1 | SE | 1.63 | 3 | 4.89 | 1 | 2.35 | 2.54 | 2.734 | 0.94 | 36 | 1 | 31.4388
FE | SE | 1 | 2.35 | 2.35 | 1 |  | 2.35 | 0.6 | 1.2 | 36 | 1 | 169.2 |  |  |  |  | r= | 1.205
PI | - | 1.75 | 3 | 5.25 | 1 |  | 5.25 | 0.592 | 1.05 | 5 | 1 | 46.5583 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 1.63 | 12.13 | 19.7719 | 1 |  | 19.7719 | 4.308 | 1.03 | 10 | 1 | 47.2726 |  |  |  |  | Rm= | 14.9276 |  |  |  | 1.5
[6 empty] | At= | 122.1038 |  |  |  |  | 294.4697 | 5.4 | 5 | 1.104 | 325.0945 | 6.7 | 0.052 | 4 | 1 | 59.3157 | 0.00022 | 1134.5897 | 52.8788 | 1134.5897 | 1459.6843 | 24.6087
Laborator P6 P11 Ti=18 °C
PE1 | SE | 5.83 | 4 | 23.32 | 1 | 6.475 | 16.845 | 2.734 | 0.94 | 36 | 1 | 208.4985
FE | SE | 1.75 | 3.7 | 6.475 | 1 |  | 6.475 | 0.6 | 1.2 | 36 | 1 | 466.2
PE1 | SV | 5.83 | 4 | 23.32 | 1 | 1.875 | 21.445 | 2.734 | 0.94 | 36 | 1 | 265.4348
FE | SV | 0.75 | 1.75 | 1.3125 | 1 |  | 1.3125 | 0.6 | 1.2 | 36 | 1 | 94.5 |  |  |  |  | r= | 1.205
FE | SV | 0.75 | 0.75 | 0.5625 | 1 |  | 0.5625 | 0.6 | 1.2 | 36 | 1 | 40.5 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 5.83 | 5.83 | 33.9889 | 1 |  | 33.9889 | 4.308 | 1.03 | 10 | 1 | 81.2641 |  |  |  |  | Rm= | 5.0201 |  |  |  | 1.5
[6 empty] | At= | 161.2578 |  |  |  |  | 1156.3974 | 5.4 | 5 | 1.104 | 1276.6627 | 18.9 | 0.052 | 4 | 1 | 135.9556 | 0.00022 | 2600.5565 | 149.1655 | 2600.5565 | 3877.2192 | 28.5183
Laborator P4 P12 Ti=18 °C
PE1 | SV | 5.73 | 4 | 22.92 | 1 | 6.1875 | 16.7325 | 2.734 | 0.94 | 36 | 1 | 207.106 |  |  |  |  | r= | 1.205
FE | SV | 2.75 | 2.25 | 6.1875 | 1 |  | 6.1875 | 0.6 | 1.2 | 36 | 1 | 445.5 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 5.73 | 5.83 | 33.4059 | 1 |  | 33.4059 | 4.308 | 1.03 | 10 | 1 | 79.8702 |  |  |  |  | Rm= | 7.8289 |  |  |  | 1.5
[6 empty] | At= | 159.2918 |  |  |  |  | 732.4762 | 5.4 | 5 | 1.104 | 808.6537 | 10 | 0.052 | 4 | 1 | 133.6236 | 0.00022 | 2555.95 | 78.9235 | 2555.95 | 3364.6037 | 25.1797
Hol acces+Casa scarii P13 Ti=18 °C
PE1 | SV | 5.75 | 3.9 | 22.425 | 1 | 4.875 | 17.55 | 2.734 | 0.94 | 36 | 1 | 217.2246 |  |  |  |  | r= | 1.205
FE | SV | 1.25 | 3.9 | 4.875 | 1 |  | 4.875 | 0.6 | 1.2 | 36 | 1 | 351 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 5.75 | 7.5 | 43.125 | 1 |  | 43.125 | 4.308 | 1.03 | 10 | 1 | 103.1076 |  |  |  |  | Rm= | 10.1672 |  |  |  | 1.5
[6 empty] | At= | 189.6 |  |  |  |  | 671.3322 | 5.4 | 5 | 1.104 | 741.1507 | 10.3 | 0.052 | 4 | 1 | 168.1875 | 0.00022 | 3217.0877 | 81.2912 | 3217.0877 | 3958.2384 | 23.5347
Zona Expozitie P14 Ti=18 °C
PE1 | SV | 5.75 | 3.9 | 22.425 | 1 | 7.7 | 14.725 | 2.734 | 0.94 | 36 | 1 | 182.2582
UE | SV | 2 | 3.85 | 7.7 | 1 |  | 7.7 | 0.6 | 1.2 | 36 | 1 | 554.4
PE1 | SE | 1 | 3.9 | 3.9 | 1 |  | 3.9 | 2.734 | 0.94 | 36 | 1 | 48.2721 |  |  |  |  | r= | 1.205
PE | NV | 1 | 3.9 | 3.9 | 1 |  | 3.9 | 2.734 | 0.94 | 36 | 1 | 48.2721 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 5.75 | 5.83 | 33.5225 | 1 |  | 33.5225 | 4.308 | 1.03 | 10 | 1 | 80.149 |  |  |  |  | Rm= | 6.2027 |  |  |  | 1.5
[6 empty] | At= | 157.369 |  |  |  |  | 913.3515 | 5.4 | 5 | 1.104 | 1008.34 | 9.8 | 0.052 | 4 | 1 | 130.7378 | 0.00022 | 2500.7495 | 77.345 | 2500.7495 | 3509.0895 | 26.8407
Laborator P2 P15 Ti=18 °C
PE1 | SV | 5.82 | 4 | 23.28 | 1 | 14.575 | 8.705 | 2.734 | 0.94 | 36 | 1 | 107.7459
FE | SV | 5.5 | 2.65 | 14.575 | 1 |  | 14.575 | 0.6 | 1.2 | 36 | 1 | 1049.4
PE1 | NV | 5.83 | 4 | 23.32 | 1 | 14.575 | 8.745 | 2.734 | 0.94 | 36 | 1 | 108.241 |  |  |  |  | r= | 1.205
FE | NV | 5.5 | 2.65 | 14.575 | 1 |  | 14.575 | 0.6 | 1.2 | 36 | 1 | 1049.4 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 5.82 | 5.83 | 33.9306 | 1 |  | 33.9306 | 4.308 | 1.03 | 10 | 1 | 81.1247 |  |  |  |  | Rm= | 2.42 |  |  |  | 1.5
[6 empty] | At= | 161.0612 |  |  |  |  | 2395.9115 | 5.4 | 5 | 1.104 | 2645.0863 | 32.6 | 0.052 | 4 | 1 | 135.7224 | 0.00022 | 2596.0958 | 257.2907 | 2596.0958 | 5241.1821 | 38.6169
Coridor P16 Ti=18 °C
PE1 | NV | 1.63 | 4 | 6.52 | 1 | 5.775 | 0.745 | 2.734 | 0.94 | 33 | 1 | 8.4528 |  |  |  |  | r= | 1.205
UE | NV | 1.5 | 3.85 | 5.775 | 1 |  | 5.775 | 0.6 | 1.2 | 33 | 1 | 381.15 |  |  |  |  | Cp= | 1.005
Pinf.1 | - | 1.63 | 12.13 | 19.7719 | 1 |  | 19.7719 | 4.308 | 1.03 | 7 | 1 | 33.0909 |  |  |  |  | Rm= | 11.6812 |  |  |  | 1.5
[6 empty] | At= | 149.6238 |  |  |  |  | 422.6936 | 5.4 | 5 | 1.104 | 466.6538 | 10.7 | 0.052 | 4 | 1 | 79.0876 | 0.00022 | 1386.7208 | 77.4108 | 1386.7208 | 1853.3745 | 23.4345
ETAJ 1
Laborator 1.1 E101 Ti=18 °C
PE1 | NV | 3.95 | 3.5 | 13.825 | 1 |  | 13.825 | 2.734 | 0.94 | 36 | 1 | 171.1185
PE1 | NE | 5.82 | 3.5 | 20.37 | 1 | 4.6375 | 15.7325 | 2.734 | 0.94 | 36 | 1 | 194.7285 |  |  |  |  | r= | 1.205
FE | NE | 0.9 | 1.75 | 1.575 | 1 |  | 1.575 | 0.6 | 1.2 | 36 | 1 | 113.4 |  |  |  |  | Cp= | 1.005
FE | NE | 1.75 | 1.75 | 3.0625 | 1 |  | 3.0625 | 0.6 | 1.2 | 36 | 1 | 220.5 |  |  |  |  | Rm= | 5.8839 |  |  |  | 1.5
[6 empty] | At= | 114.368 |  |  |  |  | 699.747 | 5.4 | 5 | 1.104 | 772.5207 | 12.3 | 0.052 | 4 | 1 | 80.4615 | 0.00022 | 1539.0662 | 97.0759 | 1539.0662 | 2311.587 | 28.7291
Laborator 1.3 E102 Ti=18 °C | [16 empty] | r= | 1.205
PE1 | NE | 5.75 | 3.5 | 20.125 | 1 | 4.375 | 15.75 | 2.734 | 0.94 | 36 | 1 | 194.9451 |  |  |  |  | Cp= | 1.005
FE | NE | 2.5 | 1.75 | 4.375 | 1 |  | 4.375 | 0.6 | 1.2 | 36 | 1 | 315 |  |  |  |  | Rm= | 8.0003 |  |  |  | 1.5
[6 empty] | At= | 113.325 |  |  |  |  | 509.9451 | 5.4 | 5 | 1.104 | 562.9794 | 8.5 | 0.052 | 4 | 1 | 79.4938 | 0.00022 | 1520.5551 | 67.085 | 1520.5551 | 2083.5346 | 26.21
Grup sanitar barbati E103 Ti=22 °C
PE1 | NE | 2.75 | 3 | 8.25 | 1 | 1.75 | 6.5 | 2.734 | 0.94 | 40 | 1 | 89.3928 |  |  |  |  | r= | 1.205
FE | NE | 1 | 1.75 | 1.75 | 1 |  | 1.75 | 0.6 | 1.2 | 40 | 1 | 140 |  |  |  |  | Cp= | 1.005
Pint. | - | 2.75 | 3.95 | 10.8625 | 1 |  | 10.8625 | 1.398 | 1.07 | 7 | 1 | 58.1975 |  |  |  |  | Rm= | 8.6129 |  |  |  | 1.5
[6 empty] | At= | 61.925 |  |  |  |  | 287.5903 | 5.4 | 5 | 1.104 | 317.4997 | 5.5 | 0.052 | 4 | 1 | 32.5875 | 0.00022 | 692.5924 | 48.231 | 692.5924 | 1010.0921 | 30.9963
Grup sanitar femei E104 Ti=22 °C
PE1 | NE | 2.75 | 3 | 8.25 | 1 | 0.9375 | 7.3125 | 2.734 | 0.94 | 40 | 1 | 100.5669 |  |  |  |  | r= | 1.205
FE | NE | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 0.6 | 1.2 | 40 | 1 | 75 |  |  |  |  | Cp= | 1.005
Pint. | - | 2.75 | 3.95 | 10.8625 | 1 |  | 10.8625 | 1.398 | 1.07 | 7 | 1 | 58.1975 |  |  |  |  | Rm= | 14.1086 |  |  |  | 1.5
[6 empty] | At= | 61.925 |  |  |  |  | 175.5669 | 5.4 | 5 | 1.104 | 193.8259 | 4 | 0.052 | 4 | 1 | 32.5875 | 0.00022 | 692.5924 | 35.0771 | 692.5924 | 886.4183 | 27.2012
Spatiu tampon E105 Ti=18 °C
PE1 | NE | 12.1 | 4.25 | 51.425 | 1 | 4 | 47.425 | 2.734 | 0.94 | 36 | 1 | 587.0015
FE | NE | 1 | 2 | 2 | 2 |  | 4 | 0.6 | 1.2 | 36 | 1 | 288
PE1 | SE | 11.9 | 4.25 | 50.575 | 1 | 8 | 42.575 | 2.734 | 0.94 | 36 | 1 | 526.9707
FE | SE | 1 | 2 | 2 | 4 |  | 8 | 0.6 | 1.2 | 36 | 1 | 576
PE1 | SV | 12.1 | 4.25 | 51.425 | 1 | 8 | 43.425 | 2.734 | 0.94 | 36 | 1 | 537.4916 |  |  |  |  | r= | 1.205
FE | SV | 1 | 2 | 2 | 4 |  | 8 | 0.6 | 1.2 | 36 | 1 | 576 |  |  |  |  | Cp= | 1.005
Psup. | - | 1 | 49.3 | 49.3 | 1 |  | 49.3 | 5.639 | 0.99 | 36 | 1 | 311.5893 |  |  |  |  | Rm= | 5.2045 |  |  |  | 1.5
[6 empty] | At= | 491.98 |  |  |  |  | 3403.0531 | 5.4 | 5 | 1.104 | 3756.9706 | 60 | 0.052 | 4 | 1 | 352.02 | 0.00022 | 6733.4327 | 473.5411 | 6733.4327 | 10490.4033 | 29.8006
Casa scarii E106 Ti=18 °C | [16 empty] | r= | 1.205
PE1 | SV | 5.72 | 3.4 | 19.448 | 1 | 4.25 | 15.198 | 2.734 | 0.94 | 36 | 1 | 188.1128 |  |  |  |  | Cp= | 1.005
FE | SV | 1.25 | 3.4 | 4.25 | 1 |  | 4.25 | 0.6 | 1.2 | 36 | 1 | 306 |  |  |  |  | Rm= | 12.8673 |  |  |  | 1.5
[6 empty] | At= | 176.608 |  |  |  |  | 494.1128 | 5.4 | 5 | 1.104 | 545.5005 | 9.3 | 0.052 | 4 | 1 | 146.8324 | 0.00022 | 2808.6077 | 73.3989 | 2808.6077 | 3354.1082 | 22.8431
Laborator 1.4 E107 Ti=18 °C | [16 empty] | r= | 1.205
PE1 | SV | 5.72 | 3.5 | 20.02 | 1 | 5.83 | 14.19 | 2.734 | 0.94 | 36 | 1 | 175.6363 |  |  |  |  | Cp= | 1.005
UE | SV | 1.1 | 2.65 | 2.915 | 2 |  | 5.83 | 0.6 | 1.2 | 36 | 1 | 419.76 |  |  |  |  | Rm= | 8.91 |  |  |  | 1.5
[6 empty] | At= | 147.3608 |  |  |  |  | 595.3963 | 5.4 | 5 | 1.104 | 657.3175 | 15 | 0.052 | 4 | 1 | 116.5164 | 0.00022 | 2228.7238 | 118.3853 | 2228.7238 | 2886.0413 | 24.7694
Laborator 1.2 E108 Ti=18 °C
PE1 | SV | 5.82 | 3.5 | 20.37 | 1 | 3.5625 | 16.8075 | 2.734 | 0.94 | 36 | 1 | 208.0343
FE | SV | 1.25 | 2.85 | 3.5625 | 1 |  | 3.5625 | 0.6 | 1.2 | 36 | 1 | 256.5 |  |  |  |  | r= | 1.205
PE1 | NV | 5.82 | 3.5 | 20.37 | 1 | 3.375 | 16.995 | 2.734 | 0.94 | 36 | 1 | 210.3551 |  |  |  |  | Cp= | 1.005
FE | NV | 1.5 | 2.25 | 3.375 | 1 |  | 3.375 | 0.6 | 1.2 | 36 | 1 | 243 |  |  |  |  | Rm= | 5.8527 |  |  |  | 1.5
[6 empty] | At= | 149.2248 |  |  |  |  | 917.8894 | 5.4 | 5 | 1.104 | 1013.3499 | 26.14 | 0.052 | 4 | 1 | 118.5534 | 0.00022 | 2267.6875 | 206.3061 | 2267.6875 | 3281.0374 | 27.6756
Coridor E109 Ti=18 °C | [16 empty] | r= | 1.205
PE1 | NV | 1.63 | 3.4 | 5.542 | 1 | 3.975 | 1.567 | 2.734 | 0.94 | 36 | 1 | 19.3955 |  |  |  |  | Cp= | 1.005
UE | NV | 1.5 | 2.65 | 3.975 | 1 |  | 3.975 | 0.6 | 1.2 | 36 | 1 | 286.2 |  |  |  |  | Rm= | 15.2899 |  |  |  | 1.5
[6 empty] | At= | 129.792 |  |  |  |  | 305.5955 | 5.4 | 5 | 1.104 | 337.3774 | 8.3 | 0.052 | 4 | 1 | 65.3956 | 0.00022 | 1250.886 | 65.5065 | 1250.886 | 1588.2634 | 24.287
ETAJ 2
Laborator 2.1 E201 Ti=18 °C
PE1 | NE | 5.82 | 3.15 | 18.333 | 1 |  | 18.333 | 2.734 | 0.94 | 36 | 1 | 226.9161
PE1 | NV | 3.95 | 3.15 | 12.4425 | 1 | 5.2875 | 7.155 | 2.734 | 0.94 | 36 | 1 | 88.5608
FE | NV | 0.75 | 1.75 | 1.3125 | 1 |  | 1.3125 | 0.6 | 1.2 | 36 | 1 | 94.5 |  |  |  |  | r= | 1.205
UE | NV | 1.5 | 2.65 | 3.975 | 1 |  | 3.975 | 0.6 | 1.2 | 36 | 1 | 286.2 |  |  |  |  | Cp= | 1.005
Psup. | - | 5.82 | 3.95 | 22.989 | 1 |  | 22.989 | 5.639 | 0.99 | 36 | 1 | 145.2967 |  |  |  |  | Rm= | 4.6003 |  |  |  | 1.5
[6 empty] | At= | 107.529 |  |  |  |  | 841.4736 | 5.4 | 5 | 1.104 | 928.9869 | 13.3 | 0.052 | 4 | 1 | 72.4154 | 0.00022 | 1385.1596 | 104.9683 | 1385.1596 | 2314.1465 | 31.9566
Laborator 2.3 E202 Ti=18 °C
PE1 | NE | 5.75 | 3.15 | 18.1125 | 1 | 4.6375 | 13.475 | 2.734 | 0.94 | 36 | 1 | 166.7864 |  |  |  |  | r= | 1.205
FE | NE | 1.75 | 2.65 | 4.6375 | 1 |  | 4.6375 | 0.6 | 1.2 | 36 | 1 | 333.9 |  |  |  |  | Cp= | 1.005
Psup. | - | 5.75 | 3.95 | 22.7125 | 1 |  | 22.7125 | 5.639 | 0.99 | 36 | 1 | 143.5491 |  |  |  |  | Rm= | 5.9532 |  |  |  | 1.5
[6 empty] | At= | 106.535 |  |  |  |  | 644.2355 | 5.4 | 5 | 1.104 | 711.236 | 8.8 | 0.052 | 4 | 1 | 71.5444 | 0.00022 | 1368.4996 | 69.4527 | 1368.4996 | 2079.7356 | 29.0692
Gr.san.barbati E203 Ti=15 °C
PE1 | NE | 2.75 | 3 | 8.25 | 1 | 1.125 | 7.125 | 2.734 | 0.94 | 33 | 1 | 80.8403 |  |  |  |  | r= | 1.205
FE | NE | 0.75 | 1.5 | 1.125 | 1 |  | 1.125 | 0.6 | 1.2 | 33 | 1 | 74.25 |  |  |  |  | Cp= | 1.005
Psup. | - | 2.75 | 3.75 | 10.3125 | 1 |  | 10.3125 | 5.639 | 0.99 | 33 | 1 | 59.7463 |  |  |  |  | Rm= | 9.1587 |  |  |  | 1.5
[6 empty] | At= | 59.625 |  |  |  |  | 214.8366 | 5.4 | 5 | 1.104 | 237.1797 | 4.5 | 0.052 | 4 | 1 | 30.9375 | 0.00022 | 542.4577 | 32.556 | 542.4577 | 779.6373 | 25.2004
Gr.san.femei E204 Ti=15 °C
PE1 | NE | 2.75 | 3 | 8.25 | 1 | 1.125 | 7.125 | 2.734 | 0.94 | 33 | 1 | 80.8403 |  |  |  |  | r= | 1.205
FE | NE | 0.75 | 1.5 | 1.125 | 1 |  | 1.125 | 0.6 | 1.2 | 33 | 1 | 74.25 |  |  |  |  | Cp= | 1.005
Psup. | - | 2.75 | 3.75 | 10.3125 | 1 |  | 10.3125 | 5.639 | 0.99 | 33 | 1 | 59.7463 |  |  |  |  | Rm= | 9.1587 |  |  |  | 1.5
[6 empty] | At= | 59.625 |  |  |  |  | 214.8366 | 5.4 | 5 | 1.104 | 237.1797 | 4.5 | 0.052 | 4 | 1 | 30.9375 | 0.00022 | 542.4577 | 32.556 | 542.4577 | 779.6373 | 25.2004
Laborator 2.5 E205 Ti=18 °C
PE2 | NE | 7.48 | 3.15 | 23.562 | 1 | 4.6 | 18.962 | 2.747 | 0.93 | 36 | 1 | 231.1058
FE | NE | 1 | 2.3 | 2.3 | 2 |  | 4.6 | 0.6 | 1.2 | 36 | 1 | 331.2
PE2 | SE | 3.75 | 3.15 | 11.8125 | 1 | 2.3 | 9.5125 | 2.747 | 0.93 | 36 | 1 | 115.9368 |  |  |  |  | r= | 1.205
FE | SE | 1 | 2.3 | 2.3 | 1 |  | 2.3 | 0.6 | 1.2 | 36 | 1 | 165.6 |  |  |  |  | Cp= | 1.005
Psup. | - | 7.48 | 3.75 | 28.05 | 1 |  | 28.05 | 5.639 | 0.99 | 36 | 1 | 177.2836 |  |  |  |  | Rm= | 4.4721 |  |  |  | 1.5
[6 empty] | At= | 126.849 |  |  |  |  | 1021.1262 | 5.4 | 5 | 1.104 | 1127.3234 | 19.8 | 0.052 | 4 | 1 | 88.3575 | 0.00022 | 1690.1008 | 156.2686 | 1690.1008 | 2817.4242 | 31.8866
Coridor E206 Ti=18 °C
PE2 | SE | 1.65 | 3 | 4.95 | 1 | 3.75 | 1.2 | 2.747 | 0.93 | 36 | 1 | 14.6254 |  |  |  |  | r= | 1.205
UE | SE | 1.5 | 2.5 | 3.75 | 1 |  | 3.75 | 0.6 | 1.2 | 36 | 1 | 270 |  |  |  |  | Cp= | 1.005
Psup. | - | 1.65 | 7.48 | 12.342 | 1 |  | 12.342 | 5.639 | 0.99 | 36 | 1 | 78.0048 |  |  |  |  | Rm= | 7.8888 |  |  |  | 1.5
[6 empty] | At= | 79.464 |  |  |  |  | 362.6302 | 5.4 | 5 | 1.104 | 400.3437 | 8 | 0.052 | 4 | 1 | 37.026 | 0.00022 | 708.2327 | 63.1388 | 708.2327 | 1108.5764 | 29.9405
Laborator 2.6 E207 Ti=18 °C
PE2 | SV | 7.48 | 3.15 | 23.562 | 1 | 4.6 | 18.962 | 2.747 | 0.93 | 36 | 1 | 231.1058
FE | SV | 1 | 2.3 | 2.3 | 2 |  | 4.6 | 0.6 | 1.2 | 36 | 1 | 331.2
PE2 | SE | 5.5 | 3.15 | 17.325 | 1 | 4.6 | 12.725 | 2.747 | 0.93 | 36 | 1 | 155.0903 |  |  |  |  | r= | 1.205
FE | SE | 1 | 2.3 | 2.3 | 2 |  | 4.6 | 0.6 | 1.2 | 36 | 1 | 331.2 |  |  |  |  | Cp= | 1.005
Psup. | - | 7.48 | 5.5 | 41.14 | 1 |  | 41.14 | 5.639 | 0.99 | 36 | 1 | 260.0159 |  |  |  |  | Rm= | 4.5131 |  |  |  | 1.5
[6 empty] | At= | 164.054 |  |  |  |  | 1308.612 | 5.4 | 5 | 1.104 | 1444.7077 | 26.4 | 0.052 | 4 | 1 | 129.591 | 0.00022 | 2478.8145 | 208.3581 | 2478.8145 | 3923.5222 | 30.2762
Casa scarii E208 Ti=18 °C
PE1 | SE | 5.7 | 3 | 17.1 | 1 | 1.625 | 15.475 | 2.734 | 0.94 | 36 | 1 | 191.5413 |  |  |  |  | r= | 1.205
FE | SE | 1.25 | 1.3 | 1.625 | 1 |  | 1.625 | 0.6 | 1.2 | 36 | 1 | 117 |  |  |  |  | Cp= | 1.005
Psup. | - | 5.7 | 7.7 | 43.89 | 1 |  | 43.89 | 5.639 | 0.99 | 36 | 1 | 277.3966 |  |  |  |  | Rm= | 10.333 |  |  |  | 1.5
[6 empty] | At= | 168.18 |  |  |  |  | 585.938 | 5.4 | 5 | 1.104 | 646.8755 | 5.1 | 0.052 | 4 | 1 | 131.67 | 0.00022 | 2518.5816 | 40.251 | 2518.5816 | 3165.4571 | 24.0408
Laborator 2.4 E209 Ti=18 °C
PE1 | SE | 5.72 | 3.15 | 18.018 | 1 | 6.625 | 11.393 | 2.734 | 0.94 | 36 | 1 | 141.0165 |  |  |  |  | r= | 1.205
FE | SE | 2.5 | 2.65 | 6.625 | 1 |  | 6.625 | 0.6 | 1.2 | 36 | 1 | 477 |  |  |  |  | Cp= | 1.005
Psup. | - | 5.72 | 5.5 | 31.46 | 1 |  | 31.46 | 5.639 | 0.99 | 36 | 1 | 198.8357 |  |  |  |  | Rm= | 5.8882 |  |  |  | 1.5
[6 empty] | At= | 133.606 |  |  |  |  | 816.8522 | 5.4 | 5 | 1.104 | 901.8048 | 10.3 | 0.052 | 4 | 1 | 99.099 | 0.00022 | 1895.564 | 81.2912 | 1895.564 | 2797.3688 | 28.228
Laborator 2.2 E210 Ti=18 °C
PE1 | SE | 5.82 | 3.15 | 18.333 | 1 | 3.9375 | 14.3955 | 2.734 | 0.94 | 36 | 1 | 178.1799
FE | SE | 1.25 | 3.15 | 3.9375 | 1 |  | 3.9375 | 0.6 | 1.2 | 36 | 1 | 283.5
PE1 | NV | 3.95 | 3.15 | 12.4425 | 1 | 2.1875 | 10.255 | 2.734 | 0.94 | 36 | 1 | 126.9309 |  |  |  |  | r= | 1.205
FE | NV | 1.25 | 1.75 | 2.1875 | 1 |  | 2.1875 | 0.6 | 1.2 | 36 | 1 | 157.5 |  |  |  |  | Cp= | 1.005
Psup. | - | 1 | 28 | 28 | 1 |  | 28 | 5.639 | 0.99 | 36 | 1 | 176.9675 |  |  |  |  | Rm= | 5.0439 |  |  |  | 1.5
[6 empty] | At= | 129.332 |  |  |  |  | 923.0783 | 5.4 | 5 | 1.104 | 1019.0785 | 14.8 | 0.052 | 4 | 1 | 88.2 | 0.00022 | 1687.0881 | 116.8068 | 1687.0881 | 2706.1666 | 30.6822
Camera server E211 Ti=15 °C
PE1 | NV | 3.5 | 3.15 | 11.025 | 1 | 5.25 | 5.775 | 2.734 | 0.94 | 33 | 1 | 65.5232 |  |  |  |  | r= | 1.205
FE | NV | 1.5 | 1.75 | 2.625 | 2 |  | 5.25 | 0.6 | 1.2 | 33 | 1 | 346.5 |  |  |  |  | Cp= | 1.005
Psup. | - | 3.5 | 2.8 | 9.8 | 1 |  | 9.8 | 5.639 | 0.99 | 33 | 1 | 56.7771 |  |  |  |  | Rm= | 4.1736 |  |  |  | 1.5
[6 empty] | At= | 59.29 |  |  |  |  | 468.8003 | 5.4 | 5 | 1.104 | 517.5555 | 6.5 | 0.052 | 4 | 1 | 30.87 | 0.00022 | 541.2741 | 47.0253 | 541.2741 | 1058.8297 | 34.2996
Coridor E212 Ti=18 °C | [16 empty] | Cp= | 1.005
Psup. | - | 1.65 | 8.65 | 14.2725 | 1 |  | 14.2725 | 5.639 | 0.99 | 36 | 1 | 90.206 |  |  | r= | 1.205 | Rm= | 36.0555 |  |  |  | 1.5
[6 empty] | At= | 90.345 |  |  |  |  | 90.206 | 5.4 | 5 | 1.104 | 99.5875 | - | 0.052 | 4 | 1 | 42.8175 | 0.00022 | 819.0124 | 7.8924 | 819.0124 | 918.5999 | 21.4538
|  | Aprilie 2014 | [17 empty] | Întocmit,
|  | Cluj Napoca | [17 empty] | ing.Bogdan Corabean

## necesar frig
Sarcina termică (de răcire) de vară a încăperilor
ELEMENTELE DE CONSTRUCTIE | [10 empty] | QPE | [7 empty] | QFE
Denumirea | Orientarea | Latime | Inaltime | Suprafata totala | Numar | Suprafata de scazut | Suprafata in calcul | ti | KPE | tsm | ts | ai | h | c1 | c2 | c3 | m | IDmax | a1 | a2 | Idmax | KFE | ts* | QPE | Qi | Qt | QFE | Qo | Qil | Qnec
- | - | m | m | mp | - | mp | mp | °C | W mpK | °C | °C | - | - | - | - | - | - | W mp | - | - | W mp | W mpK | °C | W | W | W | W | W | W | W
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 12 | 9 | 10 | 11 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31
PARTER
Laborator P1 P01
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.58778 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.34556 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.32833 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.31667 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 4.5 | 4 | 18 | 1 | 0 | 18 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 98.1699
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.31667 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.35222 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.34556 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV | 4.08 | 4 | 16.32 | 1 | 0.9375 | 15.3825 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 83.8944
FE | NV | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.30611 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 16.4089 | 20.3703 | 36.7792
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0.44333 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 182.0643 | 36.7792 |  |  | 393 | 4000 | 4611.8435
Incapere tampon P02
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 0 | 0 |  |  |  | 4000 | 4000
Echipamente P1 si P3 P03
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 2.5 | 2.7 | 6.75 | 1 | 1.89 | 4.86 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 26.5059
UE | NE | 0.9 | 2.1 | 1.89 | 1 |  | 1.89 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 41.0665 | 41.0665
PE | SE | 2 | 2.7 | 5.4 | 1 | 0 | 5.4 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 31.3313
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV | 2 | 2.7 | 5.4 | 1 | 0.9375 | 4.4625 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 24.338
FE | NV | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 20.3703 | 20.3703
Psup |  | 2 | 2.5 | 5 | 1 | 0 | 5 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 10.08
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 92.2551 | 61.4369 |  |  |  | 8000 | 8153.692
Laborator P3 P04
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 4.35 | 4 | 17.4 | 1 | 0.9375 | 16.4625 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 89.7846
FE | NE | 0.75 | 1.25 | 0.9375 | 1 |  | 0.9375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 20.3703 | 20.3703
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 89.7846 | 20.3703 |  |  | 393 | 6500 | 7003.1549
Laborator P5 P09
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 6.125 | 4 | 24.5 | 1 | 1.7625 | 22.7375 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 124.0077
FE | NE | 0.75 | 2.35 | 1.7625 | 1 |  | 1.7625 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 38.2962 | 38.2962
PE | SE | 3.95 | 4 | 15.8 | 1 | 5.2875 | 10.5125 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 60.9945
FE | SE | 0.75 | 2.35 | 1.7625 | 3 |  | 5.2875 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 123.2781 | 123.2781
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 185.0022 | 161.5743 |  |  | 524 | 3000 | 3870.5764
Laborator P6 P11
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE | 5.83 | 4 | 23.32 | 1 | 6.475 | 16.845 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 97.7362
FE | SE | 1.75 | 3.7 | 6.475 | 1 |  | 6.475 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 150.9646 | 150.9646
PE | SV | 5.83 | 4 | 23.32 | 1 | 1.88 | 21.44 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 61.7472
FE | SV | 1 | 1.88 | 1.88 | 1 |  | 1.88 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 43.8322 | 43.8322
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 159.4834 | 194.7968 |  |  | 524 | 2000 | 2878.2803
Laborator P4 P12
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV | 5.73 | 4 | 22.92 | 1 | 6.1875 | 16.7325 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 97.0835
FE | SV | 2.75 | 2.25 | 6.1875 | 1 |  | 6.1875 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 144.2616 | 144.2616
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 97.0835 | 144.2616 |  |  | 524 | 2000 | 2765.3451
Zona Expozitie P14
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE | 1 | 3.9 | 3.9 | 1 | 0 | 3.9 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 22.6282
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV | 5.75 | 3.9 | 22.425 | 1 | 7.7 | 14.725 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 85.4358
FE | SV | 2 | 3.85 | 7.7 | 1 |  | 7.7 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 179.5255 | 179.5255
PE | NV | 1 | 3.9 | 3.9 | 1 | 0 | 3.9 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 21.2701
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 129.3341 | 179.5255 |  |  | 1310 | 2000 | 3618.8596
Laborator P2 P15
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV | 5.82 | 4 | 23.28 | 1 | 14.575 | 8.705 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 25.0704
FE | SV | 5.5 | 2.65 | 14.575 | 1 |  | 14.575 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 339.8161 | 339.8161
PE | NV | 5.83 | 4 | 23.32 | 1 | 14.575 | 8.745 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 47.6942
FE | NV | 5.5 | 2.65 | 14.575 | 1 |  | 14.575 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 316.6905 | 316.6905
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 72.7646 | 656.5066 |  |  | 524 | 3000 | 4253.2712
ETAJ 1
Laborator 1.1 E101
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 5.82 | 3.5 | 20.37 | 1 | 4.64 | 15.73 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 85.7896
FE | NE | 1 | 4.64 | 4.64 | 1 |  | 4.64 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 100.8195 | 100.8195
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV | 3.95 | 3.5 | 13.825 | 1 | 0 | 13.825 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 75.4
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 161.1896 | 100.8195 |  |  | 524 | 3000 | 3786.009
Laborator 1.3 E102
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 5.75 | 3.5 | 20.125 | 1 | 4.375 | 15.75 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 85.8987
FE | NE | 2.5 | 1.75 | 4.375 | 1 |  | 4.375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 95.0615 | 95.0615
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 85.8987 | 95.0615 |  |  | 524 | 2000 | 2704.9601
Spatiu tampon E105
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 12.1 | 4.25 | 51.425 | 1 | 4 | 47.425 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 258.6505
FE | NE | 1 | 2 | 2 | 2 |  | 4 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 86.9133 | 86.9133
PE | SE | 11.9 | 4.25 | 50.575 | 1 | 2 | 48.575 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 139.896
FE | SE | 1 | 2 | 2 | 1 |  | 2 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV | 12.1 | 4.25 | 51.425 | 1 | 2 | 49.425 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 286.7684
FE | SV | 1 | 2 | 2 | 1 |  | 2 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 46.63 | 46.63
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  | 1 | 49.3 | 49.3 | 1 | 0 | 49.3 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 99.3888
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 784.7037 | 133.5433 |  |  | 524 | 2000 | 3442.247
Laborator 1.4 E107
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV | 5.72 | 3.5 | 20.02 | 1 | 5.83 | 14.19 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 82.3317
UE | SV | 1.1 | 2.65 | 2.915 | 2 |  | 5.83 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 135.9264 | 135.9264
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 82.3317 | 135.9264 |  |  | 524 | 2000 | 2742.2581
Laborator 1.2 E108
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV | 5.82 | 3.5 | 20.37 | 1 | 3.5625 | 16.8075 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 48.4056
FE | SV | 1.25 | 2.85 | 3.5625 | 1 |  | 3.5625 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 83.0597 | 83.0597
PE | NV | 5.82 | 3.5 | 20.37 | 1 | 3.375 | 16.995 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 92.6888
FE | NV | 1.5 | 2.25 | 3.375 | 1 |  | 3.375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 73.3331 | 73.3331
Psup |  |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 0
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 141.0944 | 156.3928 |  |  | 524 | 3000 | 3821.4872
ETAJ 2
Laborator 2.1 E201
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 5.82 | 3.15 | 18.333 | 1 | 0 | 18.333 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 99.9861
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV | 3.95 | 3.15 | 12.4425 | 1 | 5.29 | 7.1525 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 39.0089
FE | NV | 1 | 5.29 | 5.29 | 1 |  | 5.29 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 114.9429 | 114.9429
Psup |  | 5.82 | 3.95 | 22.989 | 1 | 0 | 22.989 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 1324.417
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 1463.412 | 114.9429 |  |  | 524 | 3000 | 5102.3549
Laborator 2.3 E202
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 5.75 | 3.15 | 18.1125 | 1 | 4.6375 | 13.475 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 73.4911
FE | NE | 1.75 | 2.65 | 4.6375 | 1 |  | 4.6375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 100.7651 | 100.7651
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  | 5.75 | 3.95 | 22.7125 | 1 | 0 | 22.7125 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 1308.4876
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 1381.9787 | 100.7651 |  |  | 524 | 3000 | 5006.7438
Laborator 2.5 E205
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE | 5.75 | 3.15 | 18.1125 | 1 | 9.275 | 8.8375 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 48.1987
FE | NE | 1.75 | 2.65 | 4.6375 | 2 |  | 9.275 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 201.5303 | 201.5303
PE | SE | 3.75 | 3.15 | 11.8125 | 1 | 2.3 | 9.5125 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 55.1924
FE | SE | 1 | 2.3 | 2.3 | 1 |  | 2.3 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  | 7.48 | 3.75 | 28.05 | 1 | 0 | 28.05 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 1615.9858
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 1719.3769 | 201.5303 |  |  | 524 | 3000 | 5444.9072
Laborator 2.6 E207
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE | 5.5 | 3.15 | 17.325 | 1 | 4.6 | 12.725 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 73.8316
FE | SE | 1 | 2.3 | 2.3 | 2 |  | 4.6 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 0 | 0
PE | SV | 7.48 | 3.15 | 23.562 | 1 | 4.6 | 18.962 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 908.8481
FE | SV | 1 | 2.3 | 2.3 | 2 |  | 4.6 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  | 7.48 | 5.5 | 41.14 | 1 | 0 | 41.14 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 2370.1125
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 3352.7922 | 0 |  |  | 524 | 3000 | 6876.7922
Laborator 2.4 E209
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE | 5.72 | 3.15 | 18.018 | 1 | 6.625 | 11.393 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 66.1032
FE | SE | 2.5 | 2.65 | 6.625 | 1 |  | 6.625 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
Psup |  | 5.72 | 5.5 | 31.46 | 1 | 0 | 31.46 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 1812.4389
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 1878.5422 | 0 |  |  | 524 | 3000 | 5402.5422
Laborator 2.2 E210
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE | 5.82 | 3.15 | 18.333 | 1 | 3.9375 | 14.3955 | 20.85 | 0.36576 | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 83.524
FE | SE | 1.25 | 3.15 | 3.9375 | 1 |  | 3.9375 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 | 1.6667 | 34.839 |  | 0 | 91.8028 | 91.8028
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV | 3.95 | 3.15 | 12.4425 | 1 | 2.1875 | 10.255 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 55.9296
FE | NV | 1.25 | 1.75 | 2.1875 | 1 |  | 2.1875 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 47.5307 | 47.5307
Psup |  | 1 | 28 | 28 | 1 | 0 | 28 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 1613.1052
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 1752.5588 | 139.3335 |  |  | 524 | 4000 | 6415.8924
Camera server E211
PE | N |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 24.9205 | 30.9205 | 8 | 0.06 | [10 empty] | 0
FE | N |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 53 | 0.85 | 1 | 147 |  | 30.9205 |  | 0 | 0 | 0
PE | S |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.819 | 33.819 | 8 | 0.06 | [10 empty] | 0
FE | S |  |  | 0 | 3 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 394 | 0.85 | 1 | 147 |  | 33.819 |  | 0 | 0 | 0
PE | E |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | E |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | V |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 29.3575 | 35.3575 | 8 | 0.06 | [10 empty] | 0
FE | V |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 575 | 0.85 | 1 | 147 |  | 35.3575 |  | 0 | 0 | 0
PE | NE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 0
FE | NE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 |  | 33.887 |  | 0 | 0 | 0
PE | SE |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SE |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | SV |  |  | 0 | 1 | 0 | 0 | 20.85 |  | 28.839 | 34.839 | 8 | 0.06 | [10 empty] | 0
FE | SV |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 514 | 0.85 | 1 | 147 |  | 34.839 |  | 0 | 0 | 0
PE | NV | 3.5 | 3.15 | 11.025 | 1 | 5.25 | 5.775 | 20.85 | 0.36576 | 27.887 | 33.887 | 8 | 0.06 | [10 empty] | 31.4962
FE | NV | 1.5 | 1.75 | 2.625 | 2 |  | 5.25 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 402 | 0.85 | 1 | 147 | 1.6667 | 33.887 |  | 0 | 114.0738 | 114.0738
Psup |  | 3.5 | 2.8 | 9.8 | 1 | 0 | 9.8 | 20.85 | 5.639 | 30.709 | 36.709 | 5.6 | 0.06 | [10 empty] | 564.5868
FEsup |  |  |  | 0 | 1 |  | 0 | 20.85 | [5 empty] | 0.9 | 0.2 | 0.65 | 0 | 734 | 0.85 | 1 | 147 |  | 36.709 |  | 0 | 0 | 0
[24 empty] | 596.083 | 114.0738 |  |  | 524 | 4000 | 5234.1568
97135.3738
Data
|  |  | Aprilie 2014 | [23 empty] | Intocmit,
ing. Bogdan Corabean
Note on K9: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K29: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K49: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K69: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K89: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K109: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K129: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K149: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K169: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K190: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K210: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K230: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K250: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K270: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K291: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K311: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K331: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K351: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K371: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K391: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on K411: user: modifica tem (aici ii 21.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L9: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L29: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L49: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L69: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L89: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L109: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L129: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L149: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L169: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L190: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L210: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L230: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L250: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L270: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L291: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L311: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L331: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L351: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L371: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L391: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on L411: user: modifica tev (aici ii 27.7) conform stas 6648-2 si A/&e(aici 0.05)-conform stas 6648-1
Note on O10: user: din stas 6648-1 tab. 3
Note on O30: user: din stas 6648-1 tab. 3
Note on O50: user: din stas 6648-1 tab. 3
Note on O70: user: din stas 6648-1 tab. 3
Note on O90: user: din stas 6648-1 tab. 3
Note on O110: user: din stas 6648-1 tab. 3
Note on O130: user: din stas 6648-1 tab. 3
Note on O150: user: din stas 6648-1 tab. 3
Note on O170: user: din stas 6648-1 tab. 3
Note on O191: user: din stas 6648-1 tab. 3
Note on O211: user: din stas 6648-1 tab. 3
Note on O231: user: din stas 6648-1 tab. 3
Note on O251: user: din stas 6648-1 tab. 3
Note on O271: user: din stas 6648-1 tab. 3
Note on O292: user: din stas 6648-1 tab. 3
Note on O312: user: din stas 6648-1 tab. 3
Note on O332: user: din stas 6648-1 tab. 3
Note on O352: user: din stas 6648-1 tab. 3
Note on O372: user: din stas 6648-1 tab. 3
Note on O392: user: din stas 6648-1 tab. 3
Note on O412: user: din stas 6648-1 tab. 3
Note on P10: user: din stas 6648-1 tab 4
Note on P30: user: din stas 6648-1 tab 4
Note on P50: user: din stas 6648-1 tab 4
Note on P70: user: din stas 6648-1 tab 4
Note on P90: user: din stas 6648-1 tab 4
Note on P110: user: din stas 6648-1 tab 4
Note on P130: user: din stas 6648-1 tab 4
Note on P150: user: din stas 6648-1 tab 4
Note on P170: user: din stas 6648-1 tab 4
Note on P191: user: din stas 6648-1 tab 4
Note on P211: user: din stas 6648-1 tab 4
Note on P231: user: din stas 6648-1 tab 4
Note on P251: user: din stas 6648-1 tab 4
Note on P271: user: din stas 6648-1 tab 4
Note on P292: user: din stas 6648-1 tab 4
Note on P312: user: din stas 6648-1 tab 4
Note on P332: user: din stas 6648-1 tab 4
Note on P352: user: din stas 6648-1 tab 4
Note on P372: user: din stas 6648-1 tab 4
Note on P392: user: din stas 6648-1 tab 4
Note on P412: user: din stas 6648-1 tab 4
Note on Q10: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q30: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q50: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q70: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q90: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q110: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q130: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q150: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q170: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q191: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q211: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q231: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q251: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q271: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q292: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q312: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q332: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q352: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q372: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q392: user: din stas 6648-1, in functie de suprf. ferestrei
Note on Q412: user: din stas 6648-1, in functie de suprf. ferestrei
Note on T10: user: din stas 6648-2
Note on T12: user: din stas 6648-2
Note on T14: user: din stas 6648-2
Note on T16: user: din stas 6648-2
Note on T18: user: din stas 6648-2
Note on T20: user: din stas 6648-2
Note on T22: user: din stas 6648-2
Note on T24: user: din stas 6648-2
Note on T26: user: din stas 6648-2
Note on T30: user: din stas 6648-2
Note on T32: user: din stas 6648-2
Note on T34: user: din stas 6648-2
Note on T36: user: din stas 6648-2
Note on T38: user: din stas 6648-2
Note on T40: user: din stas 6648-2
Note on T42: user: din stas 6648-2
Note on T44: user: din stas 6648-2
Note on T46: user: din stas 6648-2
Note on T50: user: din stas 6648-2
Note on T52: user: din stas 6648-2
Note on T54: user: din stas 6648-2
Note on T56: user: din stas 6648-2
Note on T58: user: din stas 6648-2
Note on T60: user: din stas 6648-2
Note on T62: user: din stas 6648-2
Note on T64: user: din stas 6648-2
Note on T66: user: din stas 6648-2
Note on T70: user: din stas 6648-2
Note on T72: user: din stas 6648-2
Note on T74: user: din stas 6648-2
Note on T76: user: din stas 6648-2
Note on T78: user: din stas 6648-2
Note on T80: user: din stas 6648-2
Note on T82: user: din stas 6648-2
Note on T84: user: din stas 6648-2
Note on T86: user: din stas 6648-2
Note on T90: user: din stas 6648-2
Note on T92: user: din stas 6648-2
Note on T94: user: din stas 6648-2
Note on T96: user: din stas 6648-2
Note on T98: user: din stas 6648-2
Note on T100: user: din stas 6648-2
Note on T102: user: din stas 6648-2
Note on T104: user: din stas 6648-2
Note on T106: user: din stas 6648-2
Note on T110: user: din stas 6648-2
Note on T112: user: din stas 6648-2
Note on T114: user: din stas 6648-2
Note on T116: user: din stas 6648-2
Note on T118: user: din stas 6648-2
Note on T120: user: din stas 6648-2
Note on T122: user: din stas 6648-2
Note on T124: user: din stas 6648-2
Note on T126: user: din stas 6648-2
Note on T130: user: din stas 6648-2
Note on T132: user: din stas 6648-2
Note on T134: user: din stas 6648-2
Note on T136: user: din stas 6648-2
Note on T138: user: din stas 6648-2
Note on T140: user: din stas 6648-2
Note on T142: user: din stas 6648-2
Note on T144: user: din stas 6648-2
Note on T146: user: din stas 6648-2
Note on T150: user: din stas 6648-2
Note on T152: user: din stas 6648-2
Note on T154: user: din stas 6648-2
Note on T156: user: din stas 6648-2
Note on T158: user: din stas 6648-2
Note on T160: user: din stas 6648-2
Note on T162: user: din stas 6648-2
Note on T164: user: din stas 6648-2
Note on T166: user: din stas 6648-2
Note on T170: user: din stas 6648-2
Note on T172: user: din stas 6648-2
Note on T174: user: din stas 6648-2
Note on T176: user: din stas 6648-2
Note on T178: user: din stas 6648-2
Note on T180: user: din stas 6648-2
Note on T182: user: din stas 6648-2
Note on T184: user: din stas 6648-2
Note on T186: user: din stas 6648-2
Note on T191: user: din stas 6648-2
Note on T193: user: din stas 6648-2
Note on T195: user: din stas 6648-2
Note on T197: user: din stas 6648-2
Note on T199: user: din stas 6648-2
Note on T201: user: din stas 6648-2
Note on T203: user: din stas 6648-2
Note on T205: user: din stas 6648-2
Note on T207: user: din stas 6648-2
Note on T211: user: din stas 6648-2
Note on T213: user: din stas 6648-2
Note on T215: user: din stas 6648-2
Note on T217: user: din stas 6648-2
Note on T219: user: din stas 6648-2
Note on T221: user: din stas 6648-2
Note on T223: user: din stas 6648-2
Note on T225: user: din stas 6648-2
Note on T227: user: din stas 6648-2
Note on T231: user: din stas 6648-2
Note on T233: user: din stas 6648-2
Note on T235: user: din stas 6648-2
Note on T237: user: din stas 6648-2
Note on T239: user: din stas 6648-2
Note on T241: user: din stas 6648-2
Note on T243: user: din stas 6648-2
Note on T245: user: din stas 6648-2
Note on T247: user: din stas 6648-2
Note on T251: user: din stas 6648-2
Note on T253: user: din stas 6648-2
Note on T255: user: din stas 6648-2
Note on T257: user: din stas 6648-2
Note on T259: user: din stas 6648-2
Note on T261: user: din stas 6648-2
Note on T263: user: din stas 6648-2
Note on T265: user: din stas 6648-2
Note on T267: user: din stas 6648-2
Note on T271: user: din stas 6648-2
Note on T273: user: din stas 6648-2
Note on T275: user: din stas 6648-2
Note on T277: user: din stas 6648-2
Note on T279: user: din stas 6648-2
Note on T281: user: din stas 6648-2
Note on T283: user: din stas 6648-2
Note on T285: user: din stas 6648-2
Note on T287: user: din stas 6648-2
Note on T292: user: din stas 6648-2
Note on T294: user: din stas 6648-2
Note on T296: user: din stas 6648-2
Note on T298: user: din stas 6648-2
Note on T300: user: din stas 6648-2
Note on T302: user: din stas 6648-2
Note on T304: user: din stas 6648-2
Note on T306: user: din stas 6648-2
Note on T308: user: din stas 6648-2
Note on T312: user: din stas 6648-2
Note on T314: user: din stas 6648-2
Note on T316: user: din stas 6648-2
Note on T318: user: din stas 6648-2
Note on T320: user: din stas 6648-2
Note on T322: user: din stas 6648-2
Note on T324: user: din stas 6648-2
Note on T326: user: din stas 6648-2
Note on T328: user: din stas 6648-2
Note on T332: user: din stas 6648-2
Note on T334: user: din stas 6648-2
Note on T336: user: din stas 6648-2
Note on T338: user: din stas 6648-2
Note on T340: user: din stas 6648-2
Note on T342: user: din stas 6648-2
Note on T344: user: din stas 6648-2
Note on T346: user: din stas 6648-2
Note on T348: user: din stas 6648-2
Note on T352: user: din stas 6648-2
Note on T354: user: din stas 6648-2
Note on T356: user: din stas 6648-2
Note on T358: user: din stas 6648-2
Note on T360: user: din stas 6648-2
Note on T362: user: din stas 6648-2
Note on T364: user: din stas 6648-2
Note on T366: user: din stas 6648-2
Note on T368: user: din stas 6648-2
Note on T372: user: din stas 6648-2
Note on T374: user: din stas 6648-2
Note on T376: user: din stas 6648-2
Note on T378: user: din stas 6648-2
Note on T380: user: din stas 6648-2
Note on T382: user: din stas 6648-2
Note on T384: user: din stas 6648-2
Note on T386: user: din stas 6648-2
Note on T388: user: din stas 6648-2
Note on T392: user: din stas 6648-2
Note on T394: user: din stas 6648-2
Note on T396: user: din stas 6648-2
Note on T398: user: din stas 6648-2
Note on T400: user: din stas 6648-2
Note on T402: user: din stas 6648-2
Note on T404: user: din stas 6648-2
Note on T406: user: din stas 6648-2
Note on T408: user: din stas 6648-2
Note on T412: user: din stas 6648-2
Note on T414: user: din stas 6648-2
Note on T416: user: din stas 6648-2
Note on T418: user: din stas 6648-2
Note on T420: user: din stas 6648-2
Note on T422: user: din stas 6648-2
Note on T424: user: din stas 6648-2
Note on T426: user: din stas 6648-2
Note on T428: user: din stas 6648-2
Note on U10: user: din stas 6648-2
Note on U12: user: din stas 6648-2
Note on U14: user: din stas 6648-2
Note on U16: user: din stas 6648-2
Note on U18: user: din stas 6648-2
Note on U20: user: din stas 6648-2
Note on U22: user: din stas 6648-2
Note on U24: user: din stas 6648-2
Note on U26: user: din stas 6648-2
Note on U30: user: din stas 6648-2
Note on U32: user: din stas 6648-2
Note on U34: user: din stas 6648-2
Note on U36: user: din stas 6648-2
Note on U38: user: din stas 6648-2
Note on U40: user: din stas 6648-2
Note on U42: user: din stas 6648-2
Note on U44: user: din stas 6648-2
Note on U46: user: din stas 6648-2
Note on U50: user: din stas 6648-2
Note on U52: user: din stas 6648-2
Note on U54: user: din stas 6648-2
Note on U56: user: din stas 6648-2
Note on U58: user: din stas 6648-2
Note on U60: user: din stas 6648-2
Note on U62: user: din stas 6648-2
Note on U64: user: din stas 6648-2
Note on U66: user: din stas 6648-2
Note on U70: user: din stas 6648-2
Note on U72: user: din stas 6648-2
Note on U74: user: din stas 6648-2
Note on U76: user: din stas 6648-2
Note on U78: user: din stas 6648-2
Note on U80: user: din stas 6648-2
Note on U82: user: din stas 6648-2
Note on U84: user: din stas 6648-2
Note on U86: user: din stas 6648-2
Note on U90: user: din stas 6648-2
Note on U92: user: din stas 6648-2
Note on U94: user: din stas 6648-2
Note on U96: user: din stas 6648-2
Note on U98: user: din stas 6648-2
Note on U100: user: din stas 6648-2
Note on U102: user: din stas 6648-2
Note on U104: user: din stas 6648-2
Note on U106: user: din stas 6648-2
Note on U110: user: din stas 6648-2
Note on U112: user: din stas 6648-2
Note on U114: user: din stas 6648-2
Note on U116: user: din stas 6648-2
Note on U118: user: din stas 6648-2
Note on U120: user: din stas 6648-2
Note on U122: user: din stas 6648-2
Note on U124: user: din stas 6648-2
Note on U126: user: din stas 6648-2
Note on U130: user: din stas 6648-2
Note on U132: user: din stas 6648-2
Note on U134: user: din stas 6648-2
Note on U136: user: din stas 6648-2
Note on U138: user: din stas 6648-2
Note on U140: user: din stas 6648-2
Note on U142: user: din stas 6648-2
Note on U144: user: din stas 6648-2
Note on U146: user: din stas 6648-2
Note on U150: user: din stas 6648-2
Note on U152: user: din stas 6648-2
Note on U154: user: din stas 6648-2
Note on U156: user: din stas 6648-2
Note on U158: user: din stas 6648-2
Note on U160: user: din stas 6648-2
Note on U162: user: din stas 6648-2
Note on U164: user: din stas 6648-2
Note on U166: user: din stas 6648-2
Note on U170: user: din stas 6648-2
Note on U172: user: din stas 6648-2
Note on U174: user: din stas 6648-2
Note on U176: user: din stas 6648-2
Note on U178: user: din stas 6648-2
Note on U180: user: din stas 6648-2
Note on U182: user: din stas 6648-2
Note on U184: user: din stas 6648-2
Note on U186: user: din stas 6648-2
Note on U191: user: din stas 6648-2
Note on U193: user: din stas 6648-2
Note on U195: user: din stas 6648-2
Note on U197: user: din stas 6648-2
Note on U199: user: din stas 6648-2
Note on U201: user: din stas 6648-2
Note on U203: user: din stas 6648-2
Note on U205: user: din stas 6648-2
Note on U207: user: din stas 6648-2
Note on U211: user: din stas 6648-2
Note on U213: user: din stas 6648-2
Note on U215: user: din stas 6648-2
Note on U217: user: din stas 6648-2
Note on U219: user: din stas 6648-2
Note on U221: user: din stas 6648-2
Note on U223: user: din stas 6648-2
Note on U225: user: din stas 6648-2
Note on U227: user: din stas 6648-2
Note on U231: user: din stas 6648-2
Note on U233: user: din stas 6648-2
Note on U235: user: din stas 6648-2
Note on U237: user: din stas 6648-2
Note on U239: user: din stas 6648-2
Note on U241: user: din stas 6648-2
Note on U243: user: din stas 6648-2
Note on U245: user: din stas 6648-2
Note on U247: user: din stas 6648-2
Note on U251: user: din stas 6648-2
Note on U253: user: din stas 6648-2
Note on U255: user: din stas 6648-2
Note on U257: user: din stas 6648-2
Note on U259: user: din stas 6648-2
Note on U261: user: din stas 6648-2
Note on U263: user: din stas 6648-2
Note on U265: user: din stas 6648-2
Note on U267: user: din stas 6648-2
Note on U271: user: din stas 6648-2
Note on U273: user: din stas 6648-2
Note on U275: user: din stas 6648-2
Note on U277: user: din stas 6648-2
Note on U279: user: din stas 6648-2
Note on U281: user: din stas 6648-2
Note on U283: user: din stas 6648-2
Note on U285: user: din stas 6648-2
Note on U287: user: din stas 6648-2
Note on U292: user: din stas 6648-2
Note on U294: user: din stas 6648-2
Note on U296: user: din stas 6648-2
Note on U298: user: din stas 6648-2
Note on U300: user: din stas 6648-2
Note on U302: user: din stas 6648-2
Note on U304: user: din stas 6648-2
Note on U306: user: din stas 6648-2
Note on U308: user: din stas 6648-2
Note on U312: user: din stas 6648-2
Note on U314: user: din stas 6648-2
Note on U316: user: din stas 6648-2
Note on U318: user: din stas 6648-2
Note on U320: user: din stas 6648-2
Note on U322: user: din stas 6648-2
Note on U324: user: din stas 6648-2
Note on U326: user: din stas 6648-2
Note on U328: user: din stas 6648-2
Note on U332: user: din stas 6648-2
Note on U334: user: din stas 6648-2
Note on U336: user: din stas 6648-2
Note on U338: user: din stas 6648-2
Note on U340: user: din stas 6648-2
Note on U342: user: din stas 6648-2
Note on U344: user: din stas 6648-2
Note on U346: user: din stas 6648-2
Note on U348: user: din stas 6648-2
Note on U352: user: din stas 6648-2
Note on U354: user: din stas 6648-2
Note on U356: user: din stas 6648-2
Note on U358: user: din stas 6648-2
Note on U360: user: din stas 6648-2
Note on U362: user: din stas 6648-2
Note on U364: user: din stas 6648-2
Note on U366: user: din stas 6648-2
Note on U368: user: din stas 6648-2
Note on U372: user: din stas 6648-2
Note on U374: user: din stas 6648-2
Note on U376: user: din stas 6648-2
Note on U378: user: din stas 6648-2
Note on U380: user: din stas 6648-2
Note on U382: user: din stas 6648-2
Note on U384: user: din stas 6648-2
Note on U386: user: din stas 6648-2
Note on U388: user: din stas 6648-2
Note on U392: user: din stas 6648-2
Note on U394: user: din stas 6648-2
Note on U396: user: din stas 6648-2
Note on U398: user: din stas 6648-2
Note on U400: user: din stas 6648-2
Note on U402: user: din stas 6648-2
Note on U404: user: din stas 6648-2
Note on U406: user: din stas 6648-2
Note on U408: user: din stas 6648-2
Note on U412: user: din stas 6648-2
Note on U414: user: din stas 6648-2
Note on U416: user: din stas 6648-2
Note on U418: user: din stas 6648-2
Note on U420: user: din stas 6648-2
Note on U422: user: din stas 6648-2
Note on U424: user: din stas 6648-2
Note on U426: user: din stas 6648-2
Note on U428: user: din stas 6648-2

## dimes radiatoare
Dimensionarea Radiatoarelor
Nr. Incapere | ti | Qnec | Q70/50 | Tip Radiator PURMO C | Qn | ct | nreal | Qinst.real
| C | (w) | (w) |  | (w/corp) |  |  | (w)
1 | 2 | 3 | 3 | 4 | 5 | 6 | 9 | 10
PARTER
S.A.V. | 18 | #REF! | #REF! | 22 600x1400 | 2393 | 1.1 | 2 | 4786
SAS + CASERIE | 20 | #REF! | #REF! | 22 600x900 | 1538 | 1.17 | 1 | 1538
DECORATOR | 20 | #REF! | #REF! | 22 600x1400 | 2393 | 1.17 | 1 | 2393
BIROU | 20 | #REF! | #REF! | 22 600x400 | 684 | 1.17 | 1 | 684
G.S. BARBATI | 20 | #REF! | #REF! | 22 600x400 | 684 | 1.17 | 1 | 684
G.S. FEMEI | 20 | #REF! | #REF! | 22 600x400 | 684 | 1.17 | 1 | 684
G.S. H. | 20 | #REF! | #REF! | 22 600x400 | 684 | 1.17 | 1 | 684
INCAPERE | 20 | #REF! | #REF! | 22 600x900 | 1538 | 1.17 | 1 | 1538
A.C.S. | 10 | #REF! | #REF! | 22 600x700 | 1196 | 0.9 | 1 | 1196
C.T. | 10 | #REF! | #REF! | 22 600x1100 | 1880 | 0.9 | 1 | 1880
ETAJ
BIROU | 20 | #REF! | #REF! | 22 600x800 | 1367 | 1.17 | 1 | 1367
VESTIAR B. | 20 | #REF! | #REF! | 22 600x1100 | 1880 | 1.17 | 1 | 1880
G.S. BARBATI | 22 | #REF! | #REF! | 22 600x400 | 684 | 1.28 | 1 | 684
G.S. FEMEI | 22 | #REF! | #REF! | 22 600x400 | 684 | 1.28 | 1 | 684
VESTIAR F. | 20 | #REF! | #REF! | 22 600x1100 | 1880 | 1.17 | 1 | 1880
BIROU | 20 | #REF! | #REF! | 22 600x1100 | 1880 | 1.17 | 1 | 1880
PROD. SECURITATE | 20 | #REF! | #REF! | 22 600x400 | 684 | 1.17 | 1 | 684
BIROU | 20 | #REF! | #REF! | 22 600x1800 | 3076 | 1.17 | 1 | 3076
BIROU | 20 | #REF! | #REF! | 22 600x1400 | 2393 | 1.17 | 1 | 2393
BIROU | 20 | #REF! | #REF! | 22 600x1400 | 2393 | 1.17 | 1 | 2393
REPAUS NEFUMATORI | 20 | #REF! | #REF! | 22 600x1600 | 2734 | 1.17 | 1 | 2734
REPAUS FUMATORI | 20 | #REF! | #REF! | 22 600x1100 | 1880 | 1.17 | 1 | 1880
INCAPERE | 20 | #REF! | #REF! | 22 600x400 | 684 | 1.17 | 1 | 684
CORIDOR | 18 | #REF! | #REF! | 22 600x1100 | 1880 | 1.1 | 1 | 1880
Cluj-Napoca, | [6 empty] | Intocmit,
Septembrie | [6 empty] | ing. Calin STAN
Note on C6: Calin:
Note on C7: Calin:
Note on C8: Calin:
Note on C9: Calin:
Note on C10: Calin:
Note on C11: Calin:
Note on C12: Calin:
Note on C13: Calin:
Note on C14: Calin:
Note on C15: Calin:
Note on C18: Calin:
Note on C19: Calin:
Note on C20: Calin:
Note on C21: Calin:
Note on C22: Calin:
Note on C23: Calin:
Note on C24: Calin:
Note on C25: Calin:
Note on C26: Calin:
Note on C27: Calin:
Note on C28: Calin:
Note on C29: Calin:
Note on C30: Calin:

## HidraREHAUrad.
9. Calculul hidraulic
Nr. | Qtrons | Qtrons | L | d | v | R | Rxl | x | Z | Rxl+Z | SUMA
trons. | W | kcal/h | m | mm | m/s | Pa/m | Pa |  | Pa | Pa | Pa
PARTER
P01 | 2393 | 2057.98 | 10 | Tv.Ms. 16x2.0 | 0.26 | 95 | 950 | 14 | 46.8468 | 996.8468 | 996.8468
P01 | 2393 | 2057.98 | 10 | Tv.Ms. 16x2.0 | 0.26 | 95 | 950 | 14 | 46.8468 | 996.8468 | 996.8468
P02 | 1538 | 1322.68 | 18 | Tv.Ms. 16x2.0 | 0.17 | 47 | 846 | 14 | 20.0277 | 866.0277 | 866.0277
P03 | 2393 | 2057.98 | 25 | Tv.Ms. 16x2.0 | 0.26 | 95 | 2375 | 14 | 46.8468 | 2421.8468 | 2421.8468
P04 | 684 | 588.24 | 14 | Tv.Ms. 16x2.0 | 0.08 | 12 | 168 | 14 | 4.4352 | 172.4352 | 172.4352
P05 | 684 | 588.24 | 8 | Tv.Ms. 16x2.0 | 0.08 | 12 | 96 | 14 | 4.4352 | 100.4352 | 100.4352
P06 | 684 | 588.24 | 17.5 | Tv.Ms. 16x2.0 | 0.08 | 12 | 210 | 14 | 4.4352 | 214.4352 | 214.4352
P07 | 684 | 588.24 | 22 | Tv.Ms. 16x2.0 | 0.08 | 12 | 264 | 14 | 4.4352 | 268.4352 | 268.4352
DC1-1E | 11453 | 9849.58 | 18 | Tv.Ol Dn 20 | 0.4 | 115 | 2070 | 10 | 79.2 | 2149.2 | 4571.0468
P10-UH3 | 1538 | 1322.68 | 40 | Tv.Ol Dn 15 | 0.11 | 15 | 600 | 10 | 5.9895 | 605.9895 | 605.9895
UH3-UH2 | 32378 | 27845.08 | 60 | Tv.Ol Dn 32 | 0.42 | 60 | 3600 | 5 | 43.659 | 3643.659 | 4249.6485
UH2-UH1 | 63218 | 54367.48 | 41 | Tv.Ol Dn 40 | 0.6 | 100 | 4100 | 5 | 89.1 | 4189.1 | 7832.759
UH1-1P | 94058 | 80889.88 | 30 | Tv.Ol Dn 50 | 0.58 | 70 | 2100 | 5 | 83.259 | 2183.259 | 6372.359
1P-CT | 95938 | 82506.68 | 10 | Tv.Ol Dn 50 | 0.59 | 72 | 720 | 9 | 155.0786 | 875.0785 | 3058.3376
PAC1-7E | 5100 | 4386 | 12 | Tv.Ol Dn 20 | 0.2 | 30 | 360 | 1007 | 1993.86 | 2353.86 | 2353.86
7E-3E | 10200 | 8772 | 14 | Tv.Ol Dn 20 | 0.38 | 100 | 1400 | 6 | 42.8868 | 1442.8868 | 3796.7468
UH1-UH2 | 17700 | 15222 | 42 | Tv.Ol Dn 25 | 0.4 | 80 | 3360 | 3309 | 26207.28 | 29567.28 | 29567.28
UH2-5E | 35400 | 30444 | 21.5 | Tv.Ol Dn 32 | 0.45 | 70 | 1505 | 6 | 60.1425 | 1565.1425 | 31132.4225
ETAJ
E11 | 684 | 588.24 | 1 | Tv.Ms. 16x2.0 | 0.08 | 12 | 12 | 14 | 4.4352 | 16.4352 | 16.4352
E12 | 1880 | 1616.8 | 16 | Tv.Ms. 16x2.0 | 0.2 | 64 | 1024 | 14 | 27.72 | 1051.72 | 1051.72
E13 | 1880 | 1616.8 | 53 | Tv.Ms. 16x2.0 | 0.2 | 64 | 3392 | 14 | 27.72 | 3419.72 | 3419.72
E14 | 684 | 588.24 | 45 | Tv.Ms. 16x2.0 | 0.08 | 12 | 540 | 14 | 4.4352 | 544.4352 | 544.4352
E15 | 3076 | 2645.36 | 35 | Tv.Ms. 16x2.0 | 0.33 | 148 | 5180 | 14 | 75.4677 | 5255.4677 | 5255.4677
E16 | 2393 | 2057.98 | 30 | Tv.Ms. 16x2.0 | 0.26 | 95 | 2850 | 14 | 46.8468 | 2896.8468 | 2896.8468
E17 | 2393 | 2057.98 | 18.5 | Tv.Ms. 16x2.0 | 0.26 | 95 | 1757.5 | 14 | 46.8468 | 1804.3468 | 1804.3468
DC2-2E | 12990 | 11171.4 | 1 | Tv.Ol Dn 20 | 0.44 | 150 | 150 | 10 | 95.832 | 245.832 | 5501.2997
E11 | 1367 | 1175.62 | 41.5 | Tv.Ms. 16x2.0 | 0.15 | 38 | 1577 | 14 | 15.5925 | 1592.5925 | 1592.5925
E12 | 1880 | 1616.8 | 18 | Tv.Ms. 16x2.0 | 0.2 | 64 | 1152 | 14 | 27.72 | 1179.72 | 1179.72
E13 | 684 | 588.24 | 1.5 | Tv.Ms. 16x2.0 | 0.08 | 12 | 18 | 14 | 4.4352 | 22.4352 | 22.4352
E14 | 684 | 588.24 | 30 | Tv.Ms. 16x2.0 | 0.08 | 12 | 360 | 14 | 4.4352 | 364.4352 | 364.4352
E15 | 1880 | 1616.8 | 28 | Tv.Ms. 16x2.0 | 0.2 | 64 | 1792 | 14 | 27.72 | 1819.72 | 1819.72
E16 | 1880 | 1616.8 | 43 | Tv.Ms. 16x2.0 | 0.2 | 64 | 2752 | 14 | 27.72 | 2779.72 | 2779.72
E17 | 684 | 588.24 | 36.5 | Tv.Ms. 16x2.0 | 0.08 | 12 | 438 | 14 | 4.4352 | 442.4352 | 442.4352
DC3-1E | 9059 | 7790.74 | 5 | Tv.Ol Dn 20 | 0.32 | 80 | 400 | 10 | 50.688 | 450.688 | 3230.408
1E-2E | 20512 | 17640.32 | 5 | Tv.Ol Dn 25 | 0.44 | 100 | 500 | 7 | 67.0824 | 567.0824 | 3797.4904
2E-3E | 33502 | 28811.72 | 43 | Tv.Ol Dn 32 | 0.42 | 60 | 2580 | 15 | 130.977 | 2710.977 | 5941.385
3E-UH1 | 43702 | 37583.72 | 24 | Tv.Ol Dn 32 | 0.55 | 100 | 2400 | 15 | 224.6062 | 2624.6062 | 6422.0967
UH1-4E | 56642 | 48712.12 | 19 | Tv.Ol Dn 40 | 0.55 | 80 | 1520 | 5 | 74.8688 | 1594.8688 | 8016.9654
4E-UH2 | 66842 | 57484.12 | 22 | Tv.Ol Dn 40 | 0.61 | 105 | 2310 | 5 | 92.0948 | 2402.0948 | 10419.0601
UH2-5E | 79782 | 68612.52 | 16.5 | Tv.Ol Dn 50 | 0.48 | 50 | 825 | 5 | 57.024 | 882.024 | 11301.0842
5E-UH3 | 89982 | 77384.52 | 24.5 | Tv.Ol Dn 50 | 0.55 | 60 | 1470 | 5 | 74.8688 | 1544.8688 | 12845.9529
UH3-6E | 102922 | 88512.92 | 36 | Tv.Ol Dn 50 | 0.6 | 80 | 2880 | 5 | 89.1 | 2969.1 | 15815.0529
6E-7E | 138322 | 118956.92 | 20 | Tv.Ol Dn 65 | 0.55 | 50 | 1000 | 13 | 194.6587 | 1194.6588 | 17009.7117
7E-8E | 156022 | 134178.92 | 150 | Tv.Ol Dn 65 | 0.6 | 60 | 9000 | 13 | 231.66 | 9231.66 | 26241.3717
8E-CT | 157218 | 135207.48 | 8 | Tv.Ol Dn 65 | 0.6 | 60 | 480 | 8 | 142.56 | 622.56 | 26863.9316
| Cluj-Napoca, | [7 empty] | Intocmit,
| Septembrie | [7 empty] | ing. Calin STAN

## Debite aer
Tabel centralizator
Nr.crt. | Nr.incapere | Denumire | Aria | Inaltime | Volum | Nr.pers. | Debit | Aer proaspat | Aer proaspat | Citire racord | Aer exhaustat | Aer exhaustat | Citire racord
|  | incapere | mp | utila | incapere |  | in functie de | caiet de sarcini | val.rotunjita | introducere |  | val rotunjita | evacuare
nr. de oameni
|  |  |  | m | mc |  |  | mc/h | mc/h | mc/s | mc/h | mc/h | mc/s
1 | P02 | SAS+Caserie | 15.63 | 4 | 62.52 | 1.9538 |  |  |  |  | 62.52 | 70 | 0.019444
2 | P04 | Decorator | 33.66 | 4 | 134.64 | 4.2075 |  |  |  |  | 134.64 | 140 | 0.038889
3 | P05 | Birou | 16.59 | 4 | 66.36 | 2.0737 |  |  |  |  | 66.36 | 70 | 0.019444
4 | P06 | G.S.B. | 13.02 | 4 | 52.08 | 1.6275 |  |  |  |  | 150 | 150 | 0.041667
5 | P07 | G.S.F. | 9.72 | 4 | 38.88 | 1.215 |  |  |  |  | 105 | 110 | 0.030556
6 | P08 | G.S.H. | 3.53 | 4 | 14.12 | 1.4412 |  |  |  |  | 45 | 50 | 0.013889
7 | P09 | Suprafata vanzare | 5678.4 | 7 | 39748.8 | 709.8 | 25 | 17745 | 17750 | 4.9306
8 | P011 | Depozit | 855.9 | 7 | 5991.3 | 20.3786 | 25 | 509.4643 | 510 | 0.14167
9 | P014 | Sera | 360.41 | 4.3 | 1549.763 | 18.0205 | 25 | 450.5125 | 460 | 0.12778
10 | P015 | T.G.B.T. | 26.45 | 4.3 | 113.735 | 3.3062 |  |  |  |  | 909.88 | 910 | 0.25278
11 | E118 | Birou | 19.98 | 2.9 | 57.942 | 2.4975 |  |  |  |  | 57.942 | 60 | 0.016667
12 | E119 | Vestiar B. | 29.33 | 2.9 | 85.057 | 3.6662 |  |  |  |  | 170.114 | 180 | 0.05
13 | E120 | G.S.B. | 8.08 | 2.9 | 23.432 | 1.01 |  |  |  |  | 155 | 160 | 0.044444
14 | E121 | G.S.F. | 8.08 | 2.9 | 23.432 | 1.01 |  |  |  |  | 120 | 120 | 0.033333
15 | E122 | Vestiar F. | 27.63 | 2.9 | 80.127 | 3.4537 |  |  |  |  | 160.254 | 170 | 0.047222
16 | E123 | Birou | 34.21 | 2.9 | 99.209 | 4.2763 |  |  |  |  | 99.209 | 100 | 0.027778
17 | E124 | Birou securitate | 13.12 | 2.9 | 38.048 | 1.64 |  |  |  |  | 38.048 | 40 | 0.011111
18 | E125 | Birou | 46.6 | 2.9 | 135.14 | 9.32 |  |  |  |  | 167.76 | 170 | 0.047222
19 | E126 | Birou | 31.12 | 2.9 | 90.248 | 3.89 |  |  |  |  | 90.248 | 100 | 0.027778
20 | E127 | Birou | 31.12 | 2.9 | 90.248 | 3.89 |  |  |  |  | 90.248 | 100 | 0.027778
21 | E128 | Repaus nefumatori | 40.64 | 2.9 | 117.856 | 5.08 |  |  |  |  | 235.712 | 240 | 0.066667
22 | E129 | Repaus fumatori | 23.5 | 2.9 | 68.15 | 2.9375 |  |  |  |  | 204.45 | 210 | 0.058333
23 | E130 | Incapere | 3.94 | 2.9 | 11.426 | 1 |  |  |  |  | 11.426 | 20 | 0.0055556
|  | Arie totala | 7330.66 | [5 empty] | 18720 |  | 18720 | 18720
Intocmit,
|  | Cluj-Napoca | [8 empty] | ing. Calin STAN
Septembrie

## Dime. Ventilari
9 CALCUL AERAULIC BRICOSTORE | [19 empty] | MEDIA
[20 empty] | 0.58778 | N | 0.25 | 0.31 | 0.39 | 0.47 | 0.54 | 0.59 | 0.62 | 0.63 | 0.69 | 0.71 | 0.72 | 0.71 | 0.68 | 0.66 | 0.64 | 0.6 | 0.54 | 0.46 | 0.37
Nr.Tr. | D | D | vec | S | d | d | dales | dales | Sreala | vreala | l | R | ∆plin | Sx | r | ∆ploc | ∆p | ∆ptot | ∆pcumulat | 0.31667 | NE | 0.16 | 0.21 | 0.28 | 0.37 | 0.43 | 0.47 | 0.47 | 0.44 | 0.4 | 0.37 | 0.34 | 0.31 | 0.29 | 0.25 | 0.23 | 0.2 | 0.18 | 0.16 | 0.14
| m³/h | m³/s | m/s | m² | m | mm | m | mm | m² | m/s | m | mmH2O/ml | mm/H2O |  |  | mm/H2O | mm/H2O |  |  | 0.32833 | E | 0.16 | 0.2 | 0.27 | 0.35 | 0.44 | 0.5 | 0.53 | 0.52 | 0.48 | 0.42 | 0.37 | 0.32 | 0.28 | 0.24 | 0.21 | 0.19 | 0.16 | 0.14 | 0.13
[20 empty] | 0.35222 | SE | 0.14 | 0.18 | 0.23 | 0.3 | 0.39 | 0.47 | 0.53 | 0.56 | 0.56 | 0.53 | 0.48 | 0.41 | 0.35 | 0.3 | 0.25 | 0.21 | 0.17 | 0.15 | 0.13
[20 empty] | 0.34556 | S | 0.11 | 0.12 | 0.15 | 0.18 | 0.23 | 0.29 | 0.37 | 0.45 | 0.51 | 0.56 | 0.57 | 0.55 | 0.5 | 0.43 | 0.36 | 0.29 | 0.23 | 0.19 | 0.13
[20 empty] | 0.34556 | SV | 0.11 | 0.11 | 0.13 | 0.15 | 0.17 | 0.2 | 0.24 | 0.29 | 0.35 | 0.43 | 0.49 | 0.55 | 0.57 | 0.56 | 0.52 | 0.45 | 0.37 | 0.3 | 0.23
[20 empty] | 0.31667 | V | 0.11 | 0.12 | 0.13 | 0.14 | 0.16 | 0.18 | 0.2 | 0.23 | 0.27 | 0.32 | 0.37 | 0.44 | 0.5 | 0.53 | 0.51 | 0.49 | 0.41 | 0.33 | 0.26
REFULARE | [19 empty] | 0.30611 | NV | 0.11 | 0.12 | 0.14 | 0.16 | 0.18 | 0.2 | 0.22 | 0.25 | 0.26 | 0.3 | 0.33 | 0.37 | 0.42 | 0.45 | 0.48 | 0.47 | 0.42 | 0.35 | 0.28
Rooftop1 | [19 empty] | 0.44333 | ORIZONTALA | 0.15 | 0.17 | 0.21 | 0.26 | 0.33 | 0.41 | 0.48 | 0.56 | 0.61 | 0.65 | 0.66 | 0.65 | 0.59 | 0.55 | 0.48 | 0.4 | 0.33 | 0.27 | 0.22
1.1 | 1200 | 0.33333 | 3 | 0.11111 | 0.37622 | 376.2218 | 0.5 | 500 | 0.19625 | 1.6985 | 4 | 0.028 | 0.112 | 1.8 | 1.18 | 0.31232 | 0.42432 | 4.2243 | 4.2243
1.2 | 2400 | 0.66667 | 3.4 | 0.19608 | 0.49978 | 499.7814 | 0.5 | 500 | 0.19625 | 3.397 | 4 | 0.025 | 0.1 | 3.4 | 1.18 | 2.3597 | 2.4597 | 2.4597 | 6.684
1.3 | 3600 | 1 | 3.8 | 0.26316 | 0.57899 | 578.9931 | 0.63 | 630 | 0.31157 | 3.2096 | 4 | 0.03 | 0.12 | 1.8 | 1.18 | 1.1152 | 1.2352 | 1.2352 | 7.9192
1.4 | 4800 | 1.3333 | 4.2 | 0.31746 | 0.63593 | 635.9309 | 0.63 | 630 | 0.31157 | 4.2795 | 4 | 0.032 | 0.128 | 1.8 | 1.18 | 1.9826 | 2.1106 | 2.1106 | 10.0298
1.5 | 6000 | 1.6667 | 4.6 | 0.36232 | 0.67938 | 679.3767 | 0.63 | 630 | 0.31157 | 5.3493 | 4 | 0.03 | 0.12 | 3.7 | 1.18 | 6.3677 | 6.4877 | 6.4877 | 16.5175
1.6 | 7200 | 2 | 5 | 0.4 | 0.71383 | 713.8306 | 0.8 | 800 | 0.5024 | 3.9809 | 4 | 0.035 | 0.14 | 1.8 | 1.18 | 1.7156 | 1.8556 | 1.8556 | 18.3731
1.7 | 8400 | 2.3333 | 5.4 | 0.4321 | 0.74192 | 741.9193 | 0.8 | 800 | 0.5024 | 4.6444 | 4 | 0.04 | 0.16 | 1.8 | 1.18 | 2.3351 | 2.4951 | 2.4951 | 20.8682
1.8 | 9600 | 2.6667 | 5.8 | 0.45977 | 0.76531 | 765.3067 | 0.8 | 800 | 0.5024 | 5.3079 | 4 | 0.045 | 0.18 | 1.8 | 1.18 | 3.05 | 3.23 | 3.23 | 24.0982
1.9 | 10800 | 3 | 6.2 | 0.48387 | 0.78511 | 785.109 | 0.8 | 800 | 0.5024 | 5.9713 | 4 | 0.055 | 0.22 | 1.8 | 1.18 | 3.8601 | 4.0801 | 4.0801 | 28.1783
1.1 | 12000 | 3.3333 | 6.6 | 0.50505 | 0.80211 | 802.1075 | 0.8 | 800 | 0.5024 | 6.6348 | 4 | 0.07 | 0.28 | 1.8 | 1.18 | 4.7656 | 5.0456 | 5.0456 | 33.2238
1.11 | 13200 | 3.6667 | 7 | 0.52381 | 0.81687 | 816.868 | 0.8 | 800 | 0.5024 | 7.2983 | 47 | 0.08 | 3.76 | 2.5 | 1.18 | 8.0088 | 11.7688 | 11.7688 | 44.9926
Rooftop2
1.1 | 1200 | 0.33333 | 3 | 0.11111 | 0.37622 | 376.2218 | 0.5 | 500 | 0.19625 | 1.6985 | 4 | 0.028 | 0.112 | 1.8 | 1.18 | 0.31232 | 0.42432 | 4.2243 | 4.2243
1.2 | 2400 | 0.66667 | 3.4 | 0.19608 | 0.49978 | 499.7814 | 0.5 | 500 | 0.19625 | 3.397 | 4 | 0.025 | 0.1 | 3.4 | 1.18 | 2.3597 | 2.4597 | 2.4597 | 6.684
1.3 | 3600 | 1 | 3.8 | 0.26316 | 0.57899 | 578.9931 | 0.63 | 630 | 0.31157 | 3.2096 | 4 | 0.03 | 0.12 | 1.8 | 1.18 | 1.1152 | 1.2352 | 1.2352 | 7.9192
1.4 | 4800 | 1.3333 | 4.2 | 0.31746 | 0.63593 | 635.9309 | 0.63 | 630 | 0.31157 | 4.2795 | 4 | 0.032 | 0.128 | 1.8 | 1.18 | 1.9826 | 2.1106 | 2.1106 | 10.0298
1.5 | 6000 | 1.6667 | 4.6 | 0.36232 | 0.67938 | 679.3767 | 0.63 | 630 | 0.31157 | 5.3493 | 4 | 0.03 | 0.12 | 3.7 | 1.18 | 6.3677 | 6.4877 | 6.4877 | 16.5175
1.6 | 7200 | 2 | 5 | 0.4 | 0.71383 | 713.8306 | 0.8 | 800 | 0.5024 | 3.9809 | 4 | 0.035 | 0.14 | 1.8 | 1.18 | 1.7156 | 1.8556 | 1.8556 | 18.3731
1.7 | 8400 | 2.3333 | 5.4 | 0.4321 | 0.74192 | 741.9193 | 0.8 | 800 | 0.5024 | 4.6444 | 4 | 0.04 | 0.16 | 1.8 | 1.18 | 2.3351 | 2.4951 | 2.4951 | 20.8682
1.8 | 9600 | 2.6667 | 5.8 | 0.45977 | 0.76531 | 765.3067 | 0.8 | 800 | 0.5024 | 5.3079 | 4 | 0.045 | 0.18 | 1.8 | 1.18 | 3.05 | 3.23 | 3.23 | 24.0982
1.9 | 10800 | 3 | 6.2 | 0.48387 | 0.78511 | 785.109 | 0.8 | 800 | 0.5024 | 5.9713 | 4 | 0.055 | 0.22 | 1.8 | 1.18 | 3.8601 | 4.0801 | 4.0801 | 28.1783
1.1 | 12000 | 3.3333 | 6.6 | 0.50505 | 0.80211 | 802.1075 | 0.8 | 800 | 0.5024 | 6.6348 | 4 | 0.07 | 0.28 | 1.8 | 1.18 | 4.7656 | 5.0456 | 5.0456 | 33.2238
1.11 | 13200 | 3.6667 | 7 | 0.52381 | 0.81687 | 816.868 | 0.8 | 800 | 0.5024 | 7.2983 | 4 | 0.08 | 0.32 | 1.8 | 1.18 | 5.7663 | 6.0863 | 6.0863 | 39.3102
1.12 | 14400 | 4 | 7.4 | 0.54054 | 0.82981 | 829.8112 | 0.8 | 800 | 0.5024 | 7.9618 | 4 | 0.082 | 0.328 | 2.5 | 1.18 | 9.5311 | 9.8591 | 9.8591 | 49.1693
Rooftop3
1.1 | 1200 | 0.33333 | 3 | 0.11111 | 0.37622 | 376.2218 | 0.5 | 500 | 0.19625 | 1.6985 | 4 | 0.028 | 0.112 | 1.8 | 1.18 | 0.31232 | 0.42432 | 4.2243 | 4.2243
1.2 | 2400 | 0.66667 | 3.4 | 0.19608 | 0.49978 | 499.7814 | 0.5 | 500 | 0.19625 | 3.397 | 4 | 0.025 | 0.1 | 3.4 | 1.18 | 2.3597 | 2.4597 | 2.4597 | 6.684
1.3 | 3600 | 1 | 3.8 | 0.26316 | 0.57899 | 578.9931 | 0.63 | 630 | 0.31157 | 3.2096 | 4 | 0.03 | 0.12 | 1.8 | 1.18 | 1.1152 | 1.2352 | 1.2352 | 7.9192
1.4 | 4800 | 1.3333 | 4.2 | 0.31746 | 0.63593 | 635.9309 | 0.63 | 630 | 0.31157 | 4.2795 | 4 | 0.032 | 0.128 | 1.8 | 1.18 | 1.9826 | 2.1106 | 2.1106 | 10.0298
1.5 | 6000 | 1.6667 | 4.6 | 0.36232 | 0.67938 | 679.3767 | 0.63 | 630 | 0.31157 | 5.3493 | 4 | 0.03 | 0.12 | 3.7 | 1.18 | 6.3677 | 6.4877 | 6.4877 | 16.5175
1.6 | 7200 | 2 | 5 | 0.4 | 0.71383 | 713.8306 | 0.8 | 800 | 0.5024 | 3.9809 | 4 | 0.035 | 0.14 | 1.8 | 1.18 | 1.7156 | 1.8556 | 1.8556 | 18.3731
1.7 | 8400 | 2.3333 | 5.4 | 0.4321 | 0.74192 | 741.9193 | 0.8 | 800 | 0.5024 | 4.6444 | 4 | 0.04 | 0.16 | 1.8 | 1.18 | 2.3351 | 2.4951 | 2.4951 | 20.8682
1.8 | 9600 | 2.6667 | 5.8 | 0.45977 | 0.76531 | 765.3067 | 0.8 | 800 | 0.5024 | 5.3079 | 4 | 0.045 | 0.18 | 1.8 | 1.18 | 3.05 | 3.23 | 3.23 | 24.0982
1.9 | 10800 | 3 | 6.2 | 0.48387 | 0.78511 | 785.109 | 0.8 | 800 | 0.5024 | 5.9713 | 4 | 0.055 | 0.22 | 1.8 | 1.18 | 3.8601 | 4.0801 | 4.0801 | 28.1783
1.1 | 12000 | 3.3333 | 6.6 | 0.50505 | 0.80211 | 802.1075 | 0.8 | 800 | 0.5024 | 6.6348 | 4 | 0.07 | 0.28 | 1.8 | 1.18 | 4.7656 | 5.0456 | 5.0456 | 33.2238
1.11 | 13200 | 3.6667 | 7 | 0.52381 | 0.81687 | 816.868 | 0.8 | 800 | 0.5024 | 7.2983 | 4 | 0.08 | 0.32 | 1.8 | 1.18 | 5.7663 | 6.0863 | 6.0863 | 39.3102
1.12 | 14400 | 4 | 7.4 | 0.54054 | 0.82981 | 829.8112 | 0.8 | 800 | 0.5024 | 7.9618 | 4 | 0.082 | 0.328 | 2.5 | 1.18 | 9.5311 | 9.8591 | 9.8591 | 49.1693
Rooftop4
1.1 | 1200 | 0.33333 | 3 | 0.11111 | 0.37622 | 376.2218 | 0.5 | 500 | 0.19625 | 1.6985 | 4 | 0.028 | 0.112 | 1.8 | 1.18 | 0.31232 | 0.42432 | 4.2243 | 4.2243
1.2 | 2400 | 0.66667 | 3.4 | 0.19608 | 0.49978 | 499.7814 | 0.5 | 500 | 0.19625 | 3.397 | 4 | 0.025 | 0.1 | 3.4 | 1.18 | 2.3597 | 2.4597 | 2.4597 | 6.684
1.3 | 3600 | 1 | 3.8 | 0.26316 | 0.57899 | 578.9931 | 0.63 | 630 | 0.31157 | 3.2096 | 4 | 0.03 | 0.12 | 1.8 | 1.18 | 1.1152 | 1.2352 | 1.2352 | 7.9192
1.4 | 4800 | 1.3333 | 4.2 | 0.31746 | 0.63593 | 635.9309 | 0.63 | 630 | 0.31157 | 4.2795 | 4 | 0.032 | 0.128 | 1.8 | 1.18 | 1.9826 | 2.1106 | 2.1106 | 10.0298
1.5 | 6000 | 1.6667 | 4.6 | 0.36232 | 0.67938 | 679.3767 | 0.63 | 630 | 0.31157 | 5.3493 | 4 | 0.03 | 0.12 | 3.7 | 1.18 | 6.3677 | 6.4877 | 6.4877 | 16.5175
1.6 | 7200 | 2 | 5 | 0.4 | 0.71383 | 713.8306 | 0.8 | 800 | 0.5024 | 3.9809 | 4 | 0.035 | 0.14 | 1.8 | 1.18 | 1.7156 | 1.8556 | 1.8556 | 18.3731
1.7 | 8400 | 2.3333 | 5.4 | 0.4321 | 0.74192 | 741.9193 | 0.8 | 800 | 0.5024 | 4.6444 | 4 | 0.04 | 0.16 | 1.8 | 1.18 | 2.3351 | 2.4951 | 2.4951 | 20.8682
1.8 | 9600 | 2.6667 | 5.8 | 0.45977 | 0.76531 | 765.3067 | 0.8 | 800 | 0.5024 | 5.3079 | 4 | 0.045 | 0.18 | 1.8 | 1.18 | 3.05 | 3.23 | 3.23 | 24.0982
1.9 | 10800 | 3 | 6.2 | 0.48387 | 0.78511 | 785.109 | 0.8 | 800 | 0.5024 | 5.9713 | 4 | 0.055 | 0.22 | 1.8 | 1.18 | 3.8601 | 4.0801 | 4.0801 | 28.1783
1.1 | 12000 | 3.3333 | 6.6 | 0.50505 | 0.80211 | 802.1075 | 0.8 | 800 | 0.5024 | 6.6348 | 4 | 0.07 | 0.28 | 1.8 | 1.18 | 4.7656 | 5.0456 | 5.0456 | 33.2238
1.11 | 13200 | 3.6667 | 7 | 0.52381 | 0.81687 | 816.868 | 0.8 | 800 | 0.5024 | 7.2983 | 4 | 0.08 | 0.32 | 1.8 | 1.18 | 5.7663 | 6.0863 | 6.0863 | 39.3102
1.12 | 14400 | 4 | 7.4 | 0.54054 | 0.82981 | 829.8112 | 0.8 | 800 | 0.5024 | 7.9618 | 4 | 0.082 | 0.328 | 2.5 | 1.18 | 9.5311 | 9.8591 | 9.8591 | 49.1693
ASPIRATIE
Ramura1
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 4 | 0.07 | 0.28 | 1.7 | 1.18 | 0.81935 | 1.0993 | 1.6993 | 1.6993
1.2 | 500 | 0.13889 | 2.9 | 0.047893 | 0.247 | 247.0017 | 0.25 | 250 | 0.049063 | 2.8309 | 0.5 | 0.055 | 0.0275 | 2 | 1.18 | 0.96394 | 0.99144 | 0.99144 | 2.6908
1.3 | 875 | 0.24306 | 3.3 | 0.073653 | 0.30631 | 306.3099 | 0.315 | 315 | 0.077892 | 3.1204 | 6.5 | 0.047 | 0.3055 | 6.5 | 1.18 | 3.8065 | 4.112 | 4.112 | 6.8028
1.4 | 1375 | 0.38194 | 3.6 | 0.1061 | 0.36763 | 367.6326 | 0.4 | 400 | 0.1256 | 3.041 | 2 | 0.04 | 0.08 | 4.5 | 1.18 | 2.5027 | 2.5827 | 2.5827 | 9.3855
Ramura1.1
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 1 | 0.07 | 0.07 | 1.7 | 1.18 | 0.81935 | 0.88935 | 1.4893 | 1.4893
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 1 | 0.065 | 0.065 | 2.5 | 1.18 | 1.7955 | 1.8605 | 1.8605 | 3.3498
1.3 | 375 | 0.10417 | 3.3 | 0.031566 | 0.20053 | 200.5269 | 0.2 | 200 | 0.0314 | 3.3174 | 0.5 | 0.07 | 0.035 | 2.8 | 1.18 | 1.8533 | 1.8883 | 1.8883 | 5.2381
Ramura1.2
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 1 | 0.07 | 0.07 | 3.8 | 1.18 | 1.8315 | 1.9015 | 2.5015 | 2.5015
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 0.5 | 0.065 | 0.0325 | 3.6 | 1.18 | 2.5855 | 2.618 | 2.618 | 5.1195
1.3 | 500 | 0.13889 | 3.3 | 0.042088 | 0.23155 | 231.5485 | 0.25 | 250 | 0.049063 | 2.8309 | 2.6 | 0.055 | 0.143 | 2 | 1.18 | 0.96394 | 1.1069 | 1.1069 | 6.2264
Ramura2
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 3 | 0.07 | 0.21 | 1.7 | 1.18 | 0.81935 | 1.0293 | 1.6293 | 1.6293
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 7.5 | 0.065 | 0.4875 | 1.4 | 1.18 | 1.0055 | 1.493 | 1.493 | 3.1223
1.3 | 375 | 0.10417 | 3.3 | 0.031566 | 0.20053 | 200.5269 | 0.2 | 200 | 0.0314 | 3.3174 | 6.5 | 0.07 | 0.455 | 2 | 1.18 | 1.3238 | 1.7788 | 1.7788 | 3.4081
1.4 | 500 | 0.13889 | 3.6 | 0.03858 | 0.22169 | 221.6908 | 0.25 | 250 | 0.049063 | 2.8309 | 3.7 | 0.055 | 0.2035 | 3.7 | 1.18 | 1.7833 | 1.9868 | 1.9868 | 5.3949
1.5 | 1000 | 0.27778 | 4 | 0.069444 | 0.29743 | 297.4294 | 0.315 | 315 | 0.077892 | 3.5662 | 3 | 0.047 | 0.141 | 5.1 | 1.18 | 3.9009 | 4.0419 | 4.0419 | 9.4368
Ramura2.1
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 4.9 | 0.07 | 0.343 | 1.7 | 1.18 | 0.81935 | 1.1623 | 1.7623 | 1.7623
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 5.5 | 0.065 | 0.3575 | 2.5 | 1.18 | 1.7955 | 2.153 | 2.153 | 3.9153
1.3 | 375 | 0.10417 | 3.3 | 0.031566 | 0.20053 | 200.5269 | 0.2 | 200 | 0.0314 | 3.3174 | 4.6 | 0.07 | 0.322 | 2.8 | 1.18 | 1.8533 | 2.1753 | 2.1753 | 3.9376
1.4 | 500 | 0.13889 | 3.6 | 0.03858 | 0.22169 | 221.6908 | 0.25 | 250 | 0.049063 | 2.8309 | 3.1 | 0.055 | 0.1705 | 1.8 | 1.18 | 0.86754 | 1.038 | 1.038 | 4.9757
Ramura3
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 3.2 | 0.07 | 0.224 | 3.4 | 1.18 | 1.6387 | 1.8627 | 2.4627 | 2.4627
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 1.1 | 0.065 | 0.0715 | 3.8 | 1.18 | 2.7291 | 2.8006 | 2.8006 | 5.2633
1.3 | 375 | 0.10417 | 3.3 | 0.031566 | 0.20053 | 200.5269 | 0.2 | 200 | 0.0314 | 3.3174 | 2.2 | 0.07 | 0.154 | 3.3 | 1.18 | 2.1842 | 2.3382 | 2.3382 | 4.8009
1.4 | 500 | 0.13889 | 3.6 | 0.03858 | 0.22169 | 221.6908 | 0.25 | 250 | 0.049063 | 2.8309 | 6.6 | 0.055 | 0.363 | 4.4 | 1.18 | 2.1207 | 2.4837 | 2.4837 | 7.2846
1.5 | 1000 | 0.27778 | 4 | 0.069444 | 0.29743 | 297.4294 | 0.315 | 315 | 0.077892 | 3.5662 | 2 | 0.047 | 0.094 | 5.1 | 1.18 | 3.9009 | 3.9949 | 3.9949 | 11.2795
Ramura4.1
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 2 | 0.07 | 0.14 | 1.7 | 1.18 | 0.81935 | 0.95935 | 1.5593 | 1.5593
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 2 | 0.065 | 0.13 | 2.5 | 1.18 | 1.7955 | 1.9255 | 1.9255 | 3.4848
Ramura5.1
1.1 | 125 | 0.034722 | 2.5 | 0.013889 | 0.13301 | 133.0145 | 0.125 | 125 | 0.012266 | 2.8309 | 2 | 0.07 | 0.14 | 1.7 | 1.18 | 0.81935 | 0.95935 | 1.5593 | 1.5593
1.2 | 250 | 0.069444 | 2.9 | 0.023946 | 0.17466 | 174.6566 | 0.16 | 160 | 0.020096 | 3.4556 | 2 | 0.065 | 0.13 | 4.4 | 1.18 | 3.16 | 3.29 | 3.29 | 4.8494
|  | Cluj-Napoca | [13 empty] | Intocmit,
|  | Sept. | 2008 | [12 empty] | ing. Calin STAN